Section VII – Terms of Reference

Content

I.	CONTEXT	2

INTRODUCTION :	2

PRESENTATION OF THE CURRENT INFRASTRUCTURE OF THE RRH:	2

DESCRIPTION OF THE RRH REHABILITATION PROJECT:	4

THE CURRENT PROGRESS OF RRH REHABILITATION STUDIES:	7

II.	SERVICES EXPECTED FROM DESIGN AND ARCHITECTURE FIRMS	7

GENERAL OBJECTIVES OF THE PROJECT:	7

DEFINITION OF THE SCOPE OF THE SERVICES EXPECTED:	7

EXPECTED RESULTS	8

INFORMATION AND ADVICE OBLIGATIONS:	8

COMPLIANCE WITH APPLICABLE STANDARDS AND LEGAL FRAMEWORK:	8

CONFORMITY WITH STANDARD PRACTICES AND TECHNIQUES:	9

OBLIGATIONS RELATED TO OBTAINING INFORMATION:	9

OBLIGATION OF VIGILANCE:	9

RELATIONS BETWEEN THE CLIENT AND THE CONTRACTOR:	9

PROJECT CONSTRAINTS:	10

III.	DETAILS OF CONSULTANT MISSIONS (SCOPE OF SERVICES, TASKS (COMPONENTS) AND EXPECTED DELIVERABLES):	10

MISSION IN TERMS OF HOSPITALIZATION PROCESSES:	10

MISSION IN TERMS OF BIOCLIMATIC CONCEPTION:	10

INCEPTION REPORT & SKETCH STUDIES :	10

PRELIMINARY DESIGN :	13

DETAILED DESIGN:	16

FINAL REPORT	19

BUILDING PERMIT :	19

CONSTRUCTION DOCUMENTS:	20

ASSISTANCE WITH THE AWARDING OF WORKS CONTRACTS:	20

CONSTRUCTION SUPERVISION PHASE :	22

GENERAL :	22

DURING STARTING PHASE OF CONTRACTOR’S WORK:	23

VISAS OF CONTRACTORS' WORKING DRAWINGS:	24

SUPERVISION OF WORK :	24

BUDGETARY CONTROL:	27

ADMINISTRATIVE MANAGEMENT OF CONTRACTORS AND SUBCONTRACTORS:	28

ASSISTANCE IN THE ACCEPTANCE OPERATIONS AND HANDOVER:	29

IV.	TEAM COMPOSITION & QUALIFICATION REQUIREMENTS FOR THE KEY EXPERTS	31

PROFILE OF THE SUPERVISING FIRM	32

PROFILE OF THE DESIGN TEAM	32

PROFILE OF THE SUPERVISION TEAM	37

V.	DURATION OF SERVICES:	41

VI.	INFORMATION PROVIDED BY THE CLIENT AND FOLLOW UP OF THE PROJECT:	42

CONTEXT

INTRODUCTION :

Ruhengeri referral Hospital was constructed in 1939 and consists of very old, scattered and substandard infrastructures which have insufficient spaces to accommodate all services of a referral and/or level two teaching hospital in Rwanda.

Ruhengeri Referral Hospital (RRH) is among eight hospitals and seventeen health centers that have been selected by the Government of Rwanda to be constructed or upgraded. In line with the Priority Area III of the National Strategy for Transformation (NST1) 2017–2024), the upgrading plan will improve access to quality healthcare for all. RRH was given the status of referral hospital to respond to the increasing need of healthcare services in Rwanda. Its location facilitates health access in both the Northern Province and in the neighboring Western province. The population growth, the epidemiological transition, the introduction of universal health coverage and the surrounding tourism context no longer allows the hospital to meet all the population’s needs. The Ruhengeri referral hospital has also been designated as a Second-degree Teaching Hospital (below a University Hospital) by the Ministry of Health. However, RRH is not yet considered a teaching hospital due to the lack of teaching capacities.

It is against this background that the government of Rwanda received a financing from Agence Française de Développement ("AFD"), for the Rehabilitation of Ruhengeri Referral Hospital. It is in that regard that Rwanda Housing Authority (RHA) seeks service from a qualified consultant firm to undertake the detailed study and supervision for rehabilitation of Ruhengeri Referral Hospital.

The consultancy Services consists of detailed design and supervision of Rehabilitation of Ruhengeri Referral Hospital by providing the architectural and engineering study and carry on with subsequent supervision of rehabilitation works.

The consultant will provide architectural and engineering study and carry on with subsequent supervision of rehabilitation works.

PRESENTATION OF THE CURRENT INFRASTRUCTURE OF THE RRH:

The current infrastructure of the RRH is located in a semi-urban context in the town of Musanze. It is connected to two main axes: The NR4 Ruhengeri-Kigali Road to the North East and a less central road to the South East. The infrastructure is built on a 38 hectares ground with a slight inclination, with a 5 meters descending slope from North to South on 150 meters, and 2 meters ascending slope from West to East on 270 meters.

The current hospital is a 320-bed pavilion hospital, with 44 buildings (the oldest dating from 1939) organized as follows:

The infrastructure is extremely constrained, with common wards of 8 to 16 beds with quasi-contiguous beds, inadequate equipment, and no functionalities between buildings.

Several buildings will have to be demolished for the rehabilitation of the hospital, including some hosting inpatient clinical services.

- 21: Internal medicine

- 22: Administration

- 23: Art Clinic

- 24: Laboratory

- 25: Cafeteria

- 27: Containers

- 30: Pediatrics

- 31: Mental Health

- 32: HIC Clinic

- 36: Mortuary

- 39: Lavatories

- 40: Lavatories

- 41: Lavatories

- 42: Technical building

- 43: Kitchen

- 44: Blood Transfusion & VIIP

The service relocation and demolition of these buildings will be done during the detailed design stage, and they are not in the scope of works to be done by the Consultancy firm in the detailed study and they are not part of the rehabilitation works to be supervised. The tenders related to the works for demolition and of the old buildings and relocation of services will be made aside.

DESCRIPTION OF THE RRH REHABILITATION PROJECT:

The rehabilitated hospital will include 550 beds in total. It will be equipped with 450 hospital conventional beds, with a significant maternal and neonatal unit of 220 beds, an infectious disease hospitalization unit of 130 beds and 100 additional beds for surgery care. It will also include 40 maternity incubators, a short-term hospitalization unit (36 beds), an ICU (36 beds), and ten operation theatres for both emergency surgery and obstetrical C-section surgery.

The total net floor area will be set at 44 272 m² while the total floor area will be set at 48 535 m² (with the addition of the service rooms areas and general circulation areas).

The expected architectural plan layout is one of a “polyblock” hospital, characterized by several main buildings connected in a wider complex. The projected infrastructure will be composed of no more than 5 separate buildings of 4 floors (G+3) as shown below, but the consultant firm will be responsible to make a detailed study of the appropriate number of blocks and storeys for each block based on the findings of their pre-design assessment and concept.

The ground floors are expected to include a main hall/outpatient clinic, a medical imaging service, the emergency unit, a delivery suite and a logistic area, as shown below:

The first floor is expected to include administrative offices and the upper floor of the outpatient clinic, an operating theatre area, an ICU, a delivery suite, and a continuation of the logistic area, as shown below:

The second floor will include an upper floor for the ICU, an inpatient surgery unit, and inpatient beds for maternal & neonatal care and general patients, as shown below:

The third floor will include additional beds for inpatient care, for both general and maternal & neonatal care. The infrastructure should accommodate for the opportunity to extend this hospital with an additional area for inpatient beds, as shown below:

Finally, the infrastructure will accommodate with the characteristics of the implantation site. Access to the emergencies will be made through the road on the Southeast, while the main entrance and the parking will be accessible through the NR4, as shown below:

THE CURRENT PROGRESS OF RRH REHABILITATION STUDIES:

The AFD, the RBC, and the RHA have been assisted by the APHPi since 2022 to conduct a full feasibility study for the rehabilitation of the RRH. To begin, in October 2022, a building diagnosis report for the existing facility was submitted by the experts. Building on this initial work, APHPi has developed a comprehensive medical program, a functional program, and a technical program with data sheets for each room. Lastly, an environmental and social study has been conducted.

All these feasibility studies will serve as the foundation for the design work. A copy of the feasibility studies will be provided to the consultant to serve as foundation for development of the detailed designs

SERVICES EXPECTED FROM DESIGN AND ARCHITECTURE FIRMS

GENERAL OBJECTIVES OF THE PROJECT:

The overall objective of the project is to improve access to healthcare for the population of the Northern Province of Rwanda. The project targets several specific objectives whose purpose is to ensure sustainable access to healthcare:

- Construction and equipment of a low-carbon and resilient hospital,

- Improvement—availability and quality—of human resources for health, in line with the priorities requested by the Ministry of Health for the District of Musanze i.e. maternal/gynecological & child health, acute medicine, and basic sciences,

- Strengthening RBC's capacity to coordinate health infrastructure projects.

The medical project of the hospital of Ruhengeri was designed to consider 1) resilience to climate change and 2) reduction of gender inequalities. Specific studies have been dedicated to these components and carried out in the feasibility studies.

The overall objective of the project is to build a 550-bed facility with at least 10 operating rooms.

The general objectives of the Consultant are the following:

- To ensure the architectural and technical design of the Project,

- To ensure architectural and technical compliance, and the execution of the work.

DEFINITION OF THE SCOPE OF THE SERVICES EXPECTED:

Rwanda Housing Authority (RHA) is hiring a consultancy firm to carry out the detailed design of rehabilitation of Ruhengeri referral hospital and after that proceed with supervision of the rehabilitation works.

The consultancy services will include the following:

- Development of all Detailed architectural and engineering designs, specifications 3D representations and renderings, illustrative diagrams, project materiality, building code analysis and implementation, and rehabilitation costs estimates for the Rehabilitation works of Ruhengeri Referral hospital in full compliance with laws and regulations governing the construction sector in Rwanda and AFD sponsored projects guidelines:

- Inception Report & Sketch studies,

- Preliminary Design,

- Detailed Design,

- Final Design Report including Preparation of the building permit file and its amendments, Construction Documents and preparation of the Tender Documents for contractors.

- Assist the Client (RHA) in preparation of the tender for hiring the contractor for works implementation:

- Technical Assistance in awarding the Works Contract(s),

- Supervision of construction works to ensure their compliance with the approved detailed designs and related construction code of practice from the commencement of the project up to the completion.

Assist the client (RHA) in the overall management of the projects through endorsement and approval of both administrative and project documents as well as reporting:

- Contract execution management, including approval of execution studies,

- Assistance with pre-acceptance, acceptance, and delivery operations, and during the year of perfect completion.

Before moving on from one phase to another, the project manager submits to the RHA and concerned stakeholders (Rwanda Biomedical Center (RBC), Ministry of Health (MoH) and Ruhengeri Referral Hospital) the file of studies he has carried out during the phase that is coming to an end and may not start the next phase until he has received a written instruction to this effect from the client, who may act in a discretionary manner in this respect. Any approval or observation formulated by the client within the framework of the above procedure may in no case be interpreted as being a validation of the work carried out such as to lessen in any way whatsoever the responsibility of the Consultant company under the present contract.

EXPECTED RESULTS

The services provided by the consultant must produce at least the following expected results:

- The Inception Report is available.

- All graphic and technical documents are prepared and available,

- The Preliminary Project Summary (PPS) is available,

- The Detailed Preliminary Design is available,

- The Tender Documents are available,

- The assistance with the procurement process has been provided,

- The production of written and graphic documents required for infrastructure works and equipment supply,

- Construction works are properly monitored and controlled, in particular by:

  - Drawing up of attachments and monthly statements of work,

  - Production of monthly work monitoring and control reports,

- Equipment installation, including user training, is properly carried out,

- Environmental and social monitoring is carried out,

- All work and equipment are accepted,

- Production of as-built plans.

INFORMATION AND ADVICE OBLIGATIONS:

The Consultant company has an obligation to provide information and general advice to the client, and undertakes, within the limits of its missions, to keep the Client fully informed of any element or event likely to have an impact on the conduct of the Project and its cost, and to provide any advice that may prove necessary to ensure that the Project is carried out in the best possible conditions for the owner.

For services for which it is responsible, the Consultant team informs the client of any new regulations established by decree, order or circular likely to be applied during the course of the project and proposes any necessary adaptations.

COMPLIANCE WITH APPLICABLE STANDARDS AND LEGAL FRAMEWORK:

In general, the project manager commits to complying with all laws and standards applicable to the present project. In addition to the prescriptions of the Code and the professional duties of the project managers, it also undertakes to observe all the general rules of urban planning, as they result from laws, decrees, circulars and all applicable national and local administrative texts.

All technical aspect of the project shall be done in accordance with Rwanda Building Code and the Rwanda Green Building Minimum Compliance System where applicable and comply with the AFD sponsored projects guidelines. The Consultant shall follow the Rwandan standards for the design. In absence of the Rwandan standard, international building standards will also be allowed. International Standards will also be accepted in instances where the suggested international building standards have been found to be superior to the Rwandan standards.

In particular, the project manager is obliged to comply with all building regulations and standards in force in the client's territory at the date of submission of the building permit application and any amendments thereto.

CONFORMITY WITH STANDARD PRACTICES AND TECHNIQUES:

Unless otherwise agreed in advance by the client, the project manager undertakes to use only standard technical methods and/or traditional materials. Standard work means work to be carried out using traditional or standardized materials and processes, in compliance with approved local standards referred to in the contracts, calculation rules and specifications and/or rules drawn up by professional organizations.

If the client wishes to use non-standard processes or methods and/or non-traditional materials, he undertakes to inform the client, obtain his prior agreement and inform him of the foreseeable consequences of their use. Should the project manager fail to fulfil any of the above obligations, he will be liable for any consequences suffered by the client, in particular in terms of refusal of warranty by the client's insurer and/or the insurers of those involved in the project, in terms of "damage to work", ten-year civil liability and non-ten-year civil liability.

OBLIGATIONS RELATED TO OBTAINING INFORMATION:

The project manager, on his own initiative, must request any meeting and ask for any information he considers necessary for the completion of his mission. It may not rely on the lack of information that it should reasonably have requested, in its capacity as a professional, to justify errors or omissions in the design of the works required for the execution of the Works.

It is the responsibility of the project manager to request in good time, under its own responsibility and subject to having informed the client in advance, directly from the competent authorities, concessionaires and public or private services, the information it needs to carry out its tasks.

OBLIGATION OF VIGILANCE:

As a rule, in carrying out its assignments, the project manager must ensure that:

- that there are no inaccuracies or contradictions in the documents of the Works Contract(s), execution drawings or plans sent to it, which could subsequently incur its liability or that of the Owner,

- that the work complies with the terms of the Works Contract(s) and the Building Permit (and any modifications thereto).

RELATIONS BETWEEN THE CLIENT AND THE CONTRACTOR:

In general, the Consultant undertakes to take into account any opinions that the client may have on the studies and proposals drawn up by the Consultant, while respecting both the architectural approach and the budget approved by the client.

The Consultant must draw the client's attention, by written notification if necessary, to any opinions expressed by the latter, the consequences of which could, in the opinion of the Consultant, be prejudicial to the correct progress of the project (impact on costs and/or deadlines, deterioration in architectural quality, non-compliance with regulations, calling into question commitments made to neighbors and/or administrative authorities, etc.). The Consultant team is prohibited from making any changes to the design on its own during its work.

PROJECT CONSTRAINTS:

The Consultant’s team carries out all its tasks in accordance with the instructions and information provided by the project owner.

All members of the Consultant’s team must comply with all these instructions and information, and the project manager must ensure that they do so as part of his role of coordinating and directing the Consultant’s team's work.

If, as part of the design studies, the project manager wishes to recommend a modification to the programming specifications that would exceed the budget approved by the project owner, this must be expressly approved by the latter.

DETAILS OF CONSULTANT MISSIONS (SCOPE OF SERVICES, TASKS (COMPONENTS) AND EXPECTED DELIVERABLES):

It is hereby specified that the detailed tasks are enunciative and non-limitative, the project manager being bound, in a general manner, to carry out all services and diligence necessary for the realization of the missions mentioned hereafter.

MISSION IN TERMS OF HOSPITALIZATION PROCESSES:

During the design phase and the implementation, the consultant must provide efficient, cost-effective and long-term solutions that take into account hospitalization processes, patient pathways and the various hospital flows, so that the customer can meet its care objectives.

The consultant's mission is therefore primarily to consider:

- the hospitalization process and its flexibility in terms of evolution: in this respect, he will be able to make complementary or alternative proposals to the program in order to guarantee maximum flexibility in the use of hospitalization units or the technical platform (particularly in the event of under-occupation); These proposals will be expected in particular for the design of operating theatres and hospitalization buildings.

- the design of the various areas within the hospital (admissions, emergency, accommodation, operating room, intensive care, etc.) and their operation.

- installation and use of equipment.

- planning the central supply system for hospital fluids (gas, water, etc.).

In general terms, the consultant is responsible for the architectural and technical translation of the hospitalization process, within the scope of his responsibility as designer and in response to the client’s program.

MISSION IN TERMS OF BIOCLIMATIC CONCEPTION:

The design and construction of the Project must follow Bioclimatic design rules as described in the functional program.

The bioclimatic design of the building will thus be characterized by the integration of the following ambitions into the design of the building:

- compactness and study of prevailing winds.

- optimal thermal performance of envelope elements.

- effective solar protection and technical design of facades.

- controlled access to natural light.

- natural ventilation for thermal comfort in non-sensitive areas.

The Consultant will also manage to achieve the certifications and labels the client wants to obtain.

INCEPTION REPORT & SKETCH STUDIES :

The consultant will be required to submit an Inception Report including the Sketch Studies within Two months excluding the validation period. The validation period will be estimated to two weeks. The consultant shall be allowed Two weeks for addressing the provided comments) after the receipt of service order for commencement of the study.

The consultant examines the site and its surroundings, assesses any constraints and evaluates the technical suggestions for construction, in particular their compatibility with existing neighboring structures.

The consultant:

- Reads and analyzes the program file and documents provided by the client,

- Analyzes administrative data and regulatory constraints, as well as technical and financial data,

- Explores the various possible solutions and proposes one or more that reflect the major elements of the program; presents the general technical provisions envisaged; indicates the completion deadlines,

- Verifies the compatibility of the recommended solution(s) with the part of the provisional financial envelope selected by the Client and allocated to the work,

- Checks the feasibility of the operation considering the various constraints of the program and the site.

- Writes an inception report with the detailed elements below and submit it to client with the sketch studies.

### Expected Deliverables:

Here, the consultant will be required to include (but not limited to) the following in its inception report:

| Section | Phase and Design Discipline |  | Deliverables |  |
| --- | --- | --- | --- | --- |
| 1 | INCEPTION REPORT |  |  |  |
| 1.1 |  | General responsibilities |  |  |
|  |  |  | 1.1.1 | Preparation of initial time schedule (linked to the Financial Model) |
|  |  |  | 1.1.2 | Preparation of initial cost estimations / Calculations (linked to Financial Model) |
|  |  |  | 1.1.3 | Providing all relevant local and international design standards, Norms, building codes for Hospitals as well as international health infrastructures design standards that will be found useful. |
|  |  |  | 1.1.4 | Review of Design stages and approval |
| 1.2 |  | Inception Report |  |  |
|  |  |  | 1.2.1 | Detailed work plans and methodology of how they intend to carry out the assignment, including but not limited to standards and regulations to comply with, BIM methodology, final deliverables list, road map, procedures and model documents, detailed team chart and privileged client contact. |
|  |  |  | 1.2.2 | Detailed note explaining their appreciation of the assignments and how the consultant intends to approach the futuristic aspect of the design and to link it to Rwanda Cultural Aspect and modern practices in medical profession. |
|  |  |  | 1.2.3 | The report of the review of the feasibility study and need assessment incorporating the challenging points and obstacles that have been mentioned in the feasibility study and can hinders the smooth delivering of the assigned works and provide the way forwards to the issues. |

| Section | Phase and Design Discipline |  | Deliverables |  |
| --- | --- | --- | --- | --- |
| 2 | SKETCH STUDIES |  |  |  |
| 2.1 |  | Geotechnical Engineering |  |  |
|  |  |  | 2.1.1 | Geotechnical survey/ investigation |
| 2.2 |  | Surveyor |  |  |
|  |  |  | 2.2.1 | Cadastral map review and confirmation |
|  |  |  | 2.2.2 | Boundary and topographical survey |
| 2.3 |  | Functional & Healthcare Planning |  |  |
|  |  |  | 2.3.1 | Review of local rules and regulations, norms and standards |
|  |  |  | 2.3.2 | Initial Schedule of Accommodation (Room list) |
|  |  |  | 2.3.3 | Hospital Brief (incl. Medical Task) according to the Business plan |
|  |  |  | 2.3.4 | Departmental space calculation (Schedule of Departments) |
|  |  |  | 2.3.5 | Workflow and pathway development |
|  |  |  | 2.3.6 | Functional Description |
|  |  |  | 2.3.7 | Functional diagrams |
|  |  |  | 2.3.8 | Input Architectural studies / model |
|  |  |  | 2.3.9 | Zoning and allocation of Departments |
|  |  |  | 2.3.10 | Input Room Equipment list |
| 2.4 |  | Medical Equipment Planning |  |  |
|  |  |  | 2.4.1 | List of main equipment according to Hospital Brief |
| 2.5 |  | Architectural Design (CSA) |  |  |
|  |  |  | 2.5.1 | Review of local rules and regulations, norms and standards |
|  |  |  | 2.5.2 | Building visualizations |
|  |  |  | 2.5.3 | General site plan |
|  |  |  | 2.5.4 | Exterior traffic schemes |
|  |  |  | 2.5.5 | Floor zoning layouts including space allocation |
|  |  |  | 2.5.6 | Floor Area Analysis |
|  |  |  | 2.5.7 | Building sections |
|  |  |  | 2.5.8 | Floor plans |
|  |  |  | 2.5.9 | Sections and elevations |
|  |  |  | 2.5.10 | Site plan |
|  |  |  | 2.5.11 | Lifts and stairs concept |
|  |  |  | 2.5.12 | Interior Design studies |
|  |  |  | 2.5.13 | General Building Description |
|  |  |  | 2.5.14 | Definition of Sample room list |
|  |  |  | 2.5.15 | Elaboration of Sample room layout sheets as per Sample room list |
|  |  |  | 2.5.16 | Elaboration of Sample room data sheets as per Sample room list |
| 2.6 |  | Structural Engineering (CSA) |  |  |
|  |  |  | 2.6.1 | Review of local rules and regulations, norms and standards |
|  |  |  | 2.6.2 | Structural Pre-calculation Report |
|  |  |  | 2.6.3 | Structural grid |
| 2.7 |  | Fire Protection Engineering |  |  |
|  |  |  | 2.7.1 | Report and recommendations: review and analysis of design compliance with local regulations, norms and standards |
|  |  |  | 2.7.2 | Fire Protection Strategy |
| 2.8 |  | Building Physics |  |  |
|  |  |  | 2.8.1 | Report and recommendations: review and analysis of design compliance with local regulations, norms and standards |
|  |  |  | 2.8.2 | Building Physics Strategy |
| 2.9 |  | Technical Building Systems Engineering (M&E) |  |  |
|  |  |  | 2.9.1 | Review of local rules and regulations, norms and standards |
|  |  |  | 2.9.2 | Electricity supply system(s) schematic design (internal, external) |
|  |  |  | 2.9.3 | Water supply system(s) schematic design (internal, external) |
|  |  |  | 2.9.4 | Sewage disposal system(s) schematic design (internal, external) |
|  |  |  | 2.9.5 | Rain- & greywater disposal system(s) schematic design (internal, external) |
|  |  |  | 2.9.6 | HVAC system(s) schematic design |
|  |  |  | 2.9.7 | Conveyance system(s) schematic design |
|  |  |  | 2.9.8 | Weak current system(s) schematic design |
|  |  |  | 2.9.9 | Gas supply system schematic design (internal, external) |
|  |  |  | 2.9.10 | Heating supply systems |
|  |  |  | 2.9.11 | Medical gases and technical gases supply system schematic design |
|  |  |  | 2.9.12 | System schematic design, other special facilities and systems |
|  |  |  | 2.9.13 | General Technical Building Systems Description |
|  |  |  | 2.9.14 | Waste water treatment plant design |
| 2.10 |  | Landscape Design |  |  |
|  |  |  | 2.10.1 | Conceptual Soft Landscape Design |
|  |  |  | 2.10.2 | Conceptual Hard Landscape Design |
| 2.11 |  | Traffic Planning |  |  |
|  |  |  | 2.11.1 | Site accessibility |
|  |  |  | 2.11.2 | Traffic Impact study |
|  |  |  | 2.11.3 | Review of local rules and regulations, norms and standards |
|  |  |  | 2.11.4 | Road design definitions, calculations, and specifications |
|  |  |  | 2.11.5 | Road design drawings |
| 2.12 |  | MEQ Planning |  |  |
|  |  |  | 2.12.1 | Conceptual medical equipment and non-medical furniture planning |
|  |  |  | 2.12.2 | Preliminary REL (room equipment list, medical equipment & non-medical furniture) |
|  |  |  | 2.12.3 | Preliminary BOQ and generic specs (medical equipment & non-medical furniture) |
|  |  |  | 2.12.4 | Floor layouts w/ main equip. location (medical equipment & non-medical furniture) |
|  |  |  | 2.12.5 | Identification of heavy fixed equipment |
| 2.13 |  | Cost Engineering |  |  |
|  |  |  | 2.13.1 | Cost monitoring and control in accordance with provided CAPEX from Financial Model |
| 2.14 |  | SKETCH STUDIES REVIEW AND APPROVAL |  |  |
|  |  |  | 2.14.2 | Review and approval of Sketch Studies package |

The inception report and sketch studies are presented to the client for approval of the recommended solution, with the possibility of certain adjustments to the program and additional studies (geological, geotechnical, environmental, or urban studies).

PRELIMINARY DESIGN :

After approval of the inception report and sketch studies by the client, the consultant continues with the studies and solutions selected. It draws up the preliminary design:

- it specifies the general composition of the buildings in terms of plans and volumes,

- checks the functional relationships of program elements and their surface areas,

- assesses the interior volumes and exterior appearance of the buildings, as well as the intended treatment of the surrounding spaces,

- proposes an overall solution reflecting the major elements of the project, and presents the technical solutions envisaged,

- verifies the compatibility of the chosen solution with the constraints of the program and the site, as well as with the various regulations, particularly those relating to health and safety,

- identifies any servitudes to be created,

- defines the operation's HQE profile (proposed technical solutions and performance),

- examines the possibilities and constraints of connection to the various networks, and carries out a technical and economic feasibility study of the various energy supply solutions,

- specifies the timetable for execution, and, where appropriate, the breakdown into functional phases,

- draws up an estimate of the projected cost of the works, and compares it with the projected financial envelope, and if necessary, proposes architectural and/or technical solutions to achieve a projected cost of the Works in line with the said projected financial envelope,

- verifies the conformity of the studies with the objectives defined in terms of Building Environmental Quality, technical solutions, and project costs. Finally, he will draw up a report which he will present at a meeting for validation of the HQE aspects by the client,

- draws up the Concessionaires file, which will be updated at the end of each phase.

In the contractual time, the consultant is required to schedule a consultative meeting with the relevant building user (Ruhengeri Referral Hospital’s representatives) together with other key stakeholders including RHA, RBC and MoH to discuss the patient flow and other special considerations for such specific use of the building.

### Expected Deliverables:

| Section | Phase and Design Discipline |  | Deliverables |  |  |
| --- | --- | --- | --- | --- | --- |
| 3 | PRELIMINARY DESIGN |  |  |  |  |
| 3.1 |  | Functional & Healthcare Planning |  |  |  |
|  |  |  | 3.1.1 | Functional Planning Consultation |  |
| 3.2 |  | Architectural Design (CSA) |  |  |  |
|  |  |  | 3.2.1 | General Building Description |  |
|  |  |  | 3.2.2 | Room list and room data sheets (architectural information) |  |
|  |  |  | 3.2.3 | Site plan |  |
|  |  |  | 3.2.4 | Floor plans |  |
|  |  |  | 3.2.5 | Building sections |  |
|  |  |  | 3.2.6 | Building elevations |  |
|  |  |  | 3.2.7 | Overview Plans |  |
|  |  |  | 3.2.8 | 3D perspectives or models |  |
|  |  |  | 3.2.9 | Key architectural details |  |
|  |  |  | 3.2.10 | Preliminary interior design |  |
|  |  |  | 3.2.11 | Sample Room Sheets |  |
|  |  |  | 3.2.12 | Schedule(s) of building component materials and finishes |  |
|  |  |  | 3.2.13 | List of Trades and detailed drawings for tender documents |  |
|  |  |  | 3.2.14 | Floor Area Analysis |  |
|  |  |  | 3.2.15 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 3.2.16 | Preparation of complete set of architectural design documentation for submission to government authorities |  |
|  |  |  | 3.2.17 | Certification of complete set of architectural design documentation for submission to government authorities |  |
|  |  |  | 3.2.18 | Assembly of complete set(s) of required design documentation from all relevant design disciplines for submission to relevant government authorities |  |
|  |  |  | 3.2.19 | Submission of certified/stamped set(s) of design documentation to relevant government authorities; follow-up and coordination |  |
| 3.3 |  | Structural Engineering (CSA) |  |  |  |
|  |  |  | 3.3.1 | Report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 3.3.2 | Structural design drawings |  |
|  |  |  | 3.3.3 | Structural design calculations |  |
|  |  |  | 3.3.4 | Structural specifications |  |
|  |  |  | 3.3.5 | Complete structural engineering design documentation for submission to government authorities |  |
| 3.4 |  | Fire Protection Engineering |  |  |  |
|  |  |  | 3.4.1 | Fire protection design drawings |  |
|  |  |  | 3.4.2 | Fire protection design definitions, calculations, and specifications |  |
|  |  |  | 3.4.3 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 3.4.4 | Preparation of complete set(s) of fire protection engineering design documentation for submission to government authorities |  |
|  |  |  | 3.4.5 | Certification of complete set(s) of fire protection engineering design documentation for submission to government authorities |  |
| 3.5 |  | Building Physics |  |  |  |
|  |  |  | 3.5.1 | Building Physics Review Report |  |
|  |  |  | 3.5.2 | Building Physics review and design drawings |  |
|  |  |  | 3.5.3 | Building Physics review and design calculations |  |
| 3.6 |  | Technical Building Systems Engineering (M&E) |  |  |  |
|  |  |  | 3.6.1 | Electricity supply system design (internal, external) |  |
|  |  |  | 3.6.2 | Water supply system design (internal, external) |  |
|  |  |  | 3.6.3 | Sewage disposal system design (internal, external including design for an appropriate Sewage Treatment Plant) |  |
|  |  |  | 3.6.4 | Rainwater and greywater disposal system design (internal, external) |  |
|  |  |  | 3.6.5 | HVAC systems design |  |
|  |  |  | 3.6.6 | Conveyance systems design |  |
|  |  |  | 3.6.7 | Weak current systems design |  |
|  |  |  | 3.6.8 | Gas supply system design (internal and external) |  |
|  |  |  | 3.6.9 | Heating supply system design |  |
|  |  |  | 3.6.10 | Medical and technical gases supply system design |  |
|  |  |  | 3.6.11 | System design, other special facilities and systems |  |
|  |  |  | 3.6.12 | General Technical Building Systems Description |  |
|  |  |  | 3.6.13 | Room data sheets - M&E information |  |
|  |  |  | 3.6.14 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 3.6.15 | Preparation of complete set(s) of technical building systems engineering design documentation for submission to government authorities |  |
|  |  |  | 3.6.16 | Certification of complete set(s) of technical building systems engineering design documentation for submission to government authorities |  |
|  |  |  | 3.6.17 | Waste water treatment plant design |  |
| 3.7 |  | Landscape Design |  |  |  |
|  |  |  | 3.7.1 | Landscape design drawings (Soft, Hard) |  |
|  |  |  | 3.7.2 | Landscape design definitions, calculations, and specifications (Soft, Hard) |  |
| 3.8 |  | Traffic Planning |  |  |  |
|  |  |  | 3.8.1 | Road design drawings |  |
|  |  |  | 3.8.2 | Road design definitions, calculations, and specifications |  |
| 3.9 |  | MEQ Planning |  |  |  |
|  |  |  | 3.9.1 | REL (room equipment list, medical equipment & non-medical furniture) |  |
|  |  |  | 3.9.2 | Bill of Quantities (BoQ - medical equipment & non-medical furniture) |  |
|  |  |  | 3.9.3 | Preliminary specifications (medical equipment & non-medical furniture) |  |
|  |  |  | 3.9.4 | Initial Loaded layouts (medical equipment & non-medical furniture) |  |
|  |  |  | 3.9.5 | Pre-Installation requirements for heavy fixed equipment |  |
|  |  |  | 3.9.6 | Sample Room data sheets - medical equipment and non-medical furniture information |  |
|  |  |  | 3.9.7 | Identification of IT System Integration Requirements |  |
| 3.10 |  | Cost Engineering |  |  |  |
|  |  |  | 3.10.1 | Cost monitoring and control in accordance with provided CAPEX from Financial Model |  |
| 3.11 |  | PRELIMINARY DESIGN REVIEW |  |  |  |
|  |  |  | 3.11.1 | Review and comment of Preliminary design package |  |

The Preliminary Design is also subject to consultation with the city, leading to any adaptations that the Consultant’s team is obliged to take into account.

The Preliminary Design is submitted to the Client for approval. The Consultant must take into account the remarks and observations made by the Client and modify the preliminary design accordingly or provide the Client with the reasons why these remarks cannot be taken into account within ten (10) working days of receipt of the client’s observations.

DETAILED DESIGN:

Once the Client has approved the preliminary design, the Consultant’s team continues with the studies and solutions selected. It draws up the detailed design, then, on the basis of this design, prepares the building permit application file.

On the basis of the Preliminary design file, the consultant:

- determines the detailed surface areas of all program elements,

- establishes the dimensions and appearance of the buildings in plans, sections and facades,

- defines the principles of construction, foundations, and structure, as well as their indicative dimensions,

- defines materials,

- justifies the technical solutions chosen, in particular for technical installations and connections,

- verifies that the solutions selected comply with applicable technical regulations and health and safety objectives,

- analyzes the HQE treatment: optimization, choice of products, processes and systems, evaluation of the project's energy aspects in terms of overall cost, based on estimated consumption forecasts,

- assists the Client in choosing the layout principles,

- draws up technical and architectural descriptions,

- analyzes the HQE treatment: optimization, choice of products, processes and systems, evaluation of the project's energy aspects in terms of overall cost, based on estimated consumption forecasts,

- assists the Client in choosing the layout principles,

- draws up technical and architectural descriptions,

- coordinates geological and hydrogeological studies commissioned by the owner,

- carries out the pre-synthesis of design studies and draws up pre-synthesis plans,

- draws up the final estimate of the provisional cost of work, broken down into separate lots, compares it with the provisional financial envelope and, if necessary, proposes architectural and/or technical solutions to achieve a provisional cost of work in line with the said provisional financial envelope,

- enables the Client to finalize the program and certain equipment choices, based on estimated investment, operating and maintenance costs.

Expected Deliverables:

| Section | Phase and Design Discipline |  | Deliverables |  |  |
| --- | --- | --- | --- | --- | --- |
| 4 | DETAILED DESIGN |  |  |  |  |
| 4.1 |  | Functional & Healthcare Planning |  |  |  |
|  |  |  | 4.1.1 | Functional Planning Consultation |  |
| 4.2 |  | Architectural Design (CSA) |  |  |  |
|  |  |  | 4.2.1 | Detailed Architectural drawings |  |
|  |  |  | 4.2.2 | Room list and room data sheets |  |
|  |  |  | 4.2.3 | Design drawings for government authority approval (as required) |  |
|  |  |  | 4.2.4 | Quantity surveying - specifications and BoQ development |  |
|  |  |  | 4.2.5 | Quantity surveying - specifications and BoQ review |  |
|  |  |  | 4.2.6 | Circulation of design documents |  |
|  |  |  | 4.2.7 | Floor Area Analysis |  |
|  |  |  | 4.2.8 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 4.2.9 | Preparation of complete set of architectural design documentation for submission to government authorities |  |
|  |  |  | 4.2.10 | Certification of complete set of architectural design documentation for submission to government authorities |  |
|  |  |  | 4.2.11 | Assembly of complete set(s) of required design documentation from all relevant design disciplines for submission to relevant government authorities |  |
|  |  |  | 4.2.12 | Submission of certified/stamped set(s) of design documentation to relevant government authorities; follow-up and coordination |  |
| 4.3 |  | Structural Engineering (CSA) |  |  |  |
|  |  |  | 4.3.1 | Detailed structural drawings |  |
|  |  |  | 4.3.2 | Structural calculations and other supporting design documentation |  |
|  |  |  | 4.3.3 | Certification of complete set of structural engineering design documentation for submission to government authorities |  |
| 4.4 |  | Fire Protection Engineering |  |  |  |
|  |  |  | 4.4.1 | Fire protection design drawings |  |
|  |  |  | 4.4.2 | Fire protection design definitions, calculations, and specifications |  |
|  |  |  | 4.4.3 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 4.4.4 | Preparation of complete set(s) of fire protection engineering design documentation for submission to government authorities |  |
|  |  |  | 4.4.5 | Certification of complete set(s) of fire protection engineering design documentation for submission to government authorities |  |
| 4.5 |  | Building Physics |  |  |  |
|  |  |  | 4.5.1 | Review and release of construction documents |  |
|  |  |  | 4.5.2 | Thermal and acoustical performance certificates |  |
|  |  |  | 4.5.3 | Noise impact assessment |  |
| 4.6 |  | Technical Building Systems Engineering (M&E) |  |  |  |
|  |  |  | 4.6.1 | Electricity supply system design (internal, external) |  |
|  |  |  | 4.6.2 | Water supply system design (internal, external) |  |
|  |  |  | 4.6.3 | Sewage disposal system design (internal, external) |  |
|  |  |  | 4.6.4 | Rainwater and greywater disposal system design (internal, external) |  |
|  |  |  | 4.6.5 | HVAC systems design |  |
|  |  |  | 4.6.6 | Conveyance systems design |  |
|  |  |  | 4.6.7 | Weak current systems design |  |
|  |  |  | 4.6.8 | Gas supply system design |  |
|  |  |  | 4.6.9 | Heating system design |  |
|  |  |  | 4.6.10 | Medical and technical gases supply system design |  |
|  |  |  | 4.6.11 | System design, special facilities and systems |  |
|  |  |  | 4.6.12 | General Technical Building Systems Description |  |
|  |  |  | 4.6.13 | Room data sheets - M&E information |  |
|  |  |  | 4.6.14 | Circulation of design documents |  |
|  |  |  | 4.6.15 | Quantity surveying |  |
|  |  |  | 4.6.16 | Pre-submission report and recommendations: review and analysis of design compliance with local regulations, norms and standards |  |
|  |  |  | 4.6.17 | Preparation of complete set(s) of technical building systems engineering design documentation for submission to government authorities |  |
|  |  |  | 4.6.18 | Certification of complete set(s) of technical building systems engineering design documentation for submission to government authorities |  |
| 4.7 |  | Landscape Design |  |  |  |
|  |  |  | 4.7.1 | Landscape design drawings (Soft, Hard) |  |
|  |  |  | 4.7.2 | Landscape design definitions, calculations, and specifications (Soft, Hard) |  |
| 4.8 |  | Traffic Planning |  |  |  |
|  |  |  | 4.8.1 | Traffic planning design drawings |  |
|  |  |  | 4.8.2 | Traffic planningdesign definitions, calculations, and specifications |  |
| 4.9 |  | MEQ Planning |  |  |  |
|  |  |  | 4.9.1 | Final BoQ and Specifications (medical equipment & non-medical furniture) |  |
|  |  |  | 4.9.2 | Final Loaded layouts (medical equipment & non-medical furniture) |  |
|  |  |  | 4.9.3 | Wall elevations (medical equipment & non-medical furniture) |  |
|  |  |  | 4.9.4 | Pre-Installation requirements (towards civil/M&E works) |  |
|  |  |  | 4.9.5 | Room data sheets - medical equipment and non-medical furniture information |  |
| 4.10 |  | Cost Engineering |  |  |  |
|  |  |  | 4.10.1 | Cost monitoring and control in accordance with provided CAPEX from Financial Model |  |
| 4.11 |  | DETAILED DESIGN REVIEW |  |  |  |
|  |  |  | 4.11.1 | Review and comment of Detailed design package |  |

During the design review session, the client reserves the right to request the consultant to provide drawings or data other than the one illustrated in the table below, if the client believes those data and drawings would help them to more understand the project or if it is judged they would be needed for smooth implementation of the project. The client also reserves the right to request from the consultant to amend the presentation of documents and drawings if they judge it necessary.

These studies enable the Client to validate the cost of the work, broken down by trades and based on a preliminary bill of quantities (the "Final Budget") and, more generally, all expenses relating to the execution of the works program.

The detailed preliminary design is submitted to the Client for approval. From receipt of the Detailed Design, the Client has a period of ten (10) working days in which to make any comments and observations to the Consultant.

The Consultant must take into account the remarks and observations made by the Client and modify the detailed design accordingly or provide the Client with the reasons why these remarks cannot be taken into account within ten (10) working days from receipt of the project owner's observations.

FINAL REPORT

BUILDING PERMIT :

The Consultant’s team is responsible for compiling and submitting all applications for administrative authorizations, such as building permits. It draws up the graphic and written documents required for the BP application file, in accordance with current regulations. It is responsible for the material preparation of the file, which it presents to the Client for signature.

In strict compliance with the provisional schedule, the consultant:

- carries out all the consultations required to obtain the BP and its amendments, with the concessionaires, administrative authorities and public services concerned,

- prepares, if necessary, the files for declarations and/or authorizations of classified installations for environmental protection and organizes, in cooperation with the project owner, their submission to the local authority, prior to the submission of the BP file,

- assists the Client in drawing up applications for authorizations (approvals, etc.) that must be obtained prior to submitting the BP application, by supplying the graphic documents drawn up by the Consultant’s team as part of the preliminary design studies, and which are necessary for drawing up said applications,

- assists the contractors appointed by the Client to draw up the impact study and the public safety and security study, by supplying any information and/or documents relevant to its design mission,

- draws up the BP file for the project and submits it to the Client for approval. This BP file, and any amendments to it, must include all the information required by regulations, or requested by the relevant authorities,

- follows up on the BP file and any amendments to it, maintaining relations with the relevant departments and consulted organizations, and providing them with all the information they need to obtain a favorable opinion as quickly as possible,

- assists the client during the public inquiry, responding if necessary to questions and requests for information from the inquiry commissioner, and taking part in any public meetings organized by the inquiry commissioner,

- after obtaining the Building Permit (and any amendments), assists the Client in handling any administrative appeals or withdrawals.

At the discretion of the client the consultant may be requested to apply for a temporary building permit for preliminary works while waiting for approvals of the full building permit process.

Expected Deliverables:

The Consultant will prepare and submit all the documents required by the authorities to process the Building Permit Application File. The Client signs all the necessary documents, including the graphics. This formality constitutes his approval of the BP application file.

Processing administrative requests:

The Client informs the project manager of all correspondence with the administrative authorities, the content of which would have an impact on the performance of the project manager's duties and undertakes to send the project manager a copy of the various administrative authorizations required to carry out the Project as soon as they are received.

In general, the project manager will draw up all the documents required to obtain the administrative authorizations needed to carry out the program, and in particular any additional documents that may be requested by the authorities.

The project manager monitors the processing of administrative applications and provides any additional information required to obtain administrative authorizations as quickly as possible.

It is responsible for relations with the authorities, informing the Client of the steps taken and all appointments made with the authorities.

Appeal:

The project manager advises the client on any appeals or objections to administrative authorizations obtained, or on the grounds for refusal of administrative authorizations, or on any changes to be made to the program to obtain refused administrative authorizations or to prevent appeals against administrative authorizations.

Similarly, in the event of an appeal against the administrative authorizations, the project manager undertakes to draw up any document, to submit any amended application or any new application for authorization likely to defeat such appeals.

CONSTRUCTION DOCUMENTS:

The construction documents are drawn up based on the detailed design documents, approved in writing by the client.

The Consultant:

- specifies, by means of plans, sections, elevations, etc., the shapes of the various elements of the construction, the nature and characteristics of the materials and the conditions of their use,

- determines the size and footprint of all structural elements and technical equipment,

- draws up a low-impact worksite charter (management of waste and other site nuisances = "green" worksite), drafts environmental specifications to be included in the tender documents,

- specifies the layout of supplies and drains for all fluids, and, depending on how the work is devolved, coordinates the information and constraints necessary for the spatial organization of the works,

- updates the concessionaire file,

- describes the works and draws up the location plans needed to understand the project,

- establishes a provisional cost of works broken down into trades based on preliminary quantities, and compares it with the final estimate of provisional cost of works established at the end of the detailed design studies, and if necessary, proposes architectural and/or technical solutions to achieve a provisional cost of works in line with the provisional cost of works approved by the Owner,

- enables the Client to set the provisional cost of the work and, based on this assessme   nt, to estimate the operating costs, and

- establishes the provisional construction schedule and determines the overall construction deadline.

Expected Deliverables:

The Expected Deliverables are detailed in the attached Table of deliverables.

Construction Documents are presented to the client for approval.

ASSISTANCE WITH THE AWARDING OF WORKS CONTRACTS:

The Consultant is involved in assisting the client with the award of the Works Contract(s), and in particular with:

- Preparing the call for tenders,

- preparing the selection of candidates and examining the applications received,

- analyzing companies' bids and, where applicable, variants to these bids,

- make the necessary adjustments to enable the client to award the works contract(s).

Prior to the tender process, the Consultant draws up price schedules (without mentioning quantities) to be used for estimating the work to be carried out by the contractors.

Preparation of Tender Documents:

The tender documents include:

- the construction documents, approved in writing by the client on completion of the studies.

In this respect, the consultant must check that the studies included in this file are sufficiently precise and complete to enable the companies consulted to gain a good understanding of the works to be carried out, and to estimate their cost and timescale without any risk of ambiguity or omission. This file must include all details (references, plans and descriptions) and all descriptive sheets (including type, reference, etc.) for elementary components (e.g. lighting fittings), equipment and finishes relating to the entire Project, including details relating to the interior architecture, roofs and surroundings of the building.

- the provisional works schedule drawn up at the end of the studies and approved by the client. This document must define the "critical" stages in the execution of the work, and

- the special technical specifications for lot "0" (General Provisions), drawn up by the project manager and approved by the client. This document defines the organization to which the company will be subject in terms of design and execution of the work.

- The consultation regulations drawn up by the client with the assistance of the Consultant’s team.

- The general administrative clauses drawn up by the Client with the assistance of the Consultant’s team.

- The particular administrative clauses and its appendices, drawn up by the client with the assistance of the Consultant’s team.

- The Particular Technical Specifications for the work to be carried out by each specialized contractor, considering the requirements of the environmental specifications and the observations of the Technical Controller.

- The model of the "Act of Engagement" provided by the client, including execution deadlines and any phasing of the work.

- The General Health and Safety Coordination Plan drawn up by the Safety Coordinator.

- All documents relating to the tender documents for the lots concerned.

- Soil and pollution study reports drawn up at the request of the owner.

- Thermal and acoustic study reports.

- The initial report drawn up by the inspection office without any unfavorable opinion.

- Specific implementation procedures (tests, controls, etc.) throughout the project.

- The submission model drawn up by the Client.

The tender documents are drawn up in accordance with the state of the art, both for the structure of the building and for each of the trades involved.

They remind us of the regulatory requirements specific to the labels sought and the energy performance targeted, and that compliance with these requirements constitutes a joint and several obligations on the part of the contractors.

They must not be the subject of an unfavorable opinion from the Technical Controller.

These documents must be sufficiently precise and detailed, and fully dimensioned so as not to give rise to any misinterpretation. They must include complete lists defining all the works and the limits of execution between specialized companies.

They must allow for tendering by separate lots, including any special foundations, earthworks and structural work lots. They must include all the information needed to understand them and to read the accompanying descriptions, so that contractors have a full understanding of the project and can establish a price. They will be supplemented by all technical information such as dimensions, sections, reservations, foundation principles, etc.

The documents making up the contractor's consultation file must enable the bidding companies to make their bids on an identical basic solution, with the possibility of proposing alternative solutions that take into account the imperatives of the program, and which would have to be approved by the project owner.

The tender documents are submitted to the Client. The Client is responsible for distributing the tender documents to the contractors.

Invitation to tender:

The client selects the companies to be consulted. The Consultant gives its opinion on the references and technical guarantees of the companies and makes any comments and reservations about those who do not appear to offer sufficient financial and/or technical guarantees.

The Client launches call for tenders  and The Consultant must be available during the bidding period to assist the client in answering any contractual or financial questions raised by the companies; at the request of the client, it forwards any clarifications required to all the companies concerned.

Examination of bids:

The client opens and analyzes the bids. The consultant  assists the client during negotiations and takes part in all meetings with contractors. They intervenes with the companies to rectify errors and bring the bids into line with the tender documents and the observations of the Technical Control Office.

The Consultant assist the client to draw up a report analyzing the bids received, in the form of a comparative analysis table. It recommends which company or companies should be selected. Together with the company or companies likely to be selected, it may propose any savings or variants to meet or even improve the target cost agreed with the client.

Finally, in consultation with the Consultant, the client selects the company or companies to carry out the work.

Should the client choose a company that has received a formal, reasoned unfavorable opinion from the Consultant, the latter cannot be held liable.

Once the bids have been submitted, the Quantity Surveyor  , with the assistance of the other members of the Consultant, will examine any variants proposed by the companies consulted, draw up his own recommendations and submit them to the client for approval. This analysis will be the subject of a report to be drawn up within twenty (20) working days of the opening of bids.

If, after detailed examination, the bids submitted by the companies consulted do not enable the provisional construction cost of the Project agreed by the client and the Consultant at the end of the studies to be respected, the Consultant will, in consultation with the client, make any corrections required to bring the construction cost within the final budget.

Finalization of the contract(s):

The Consultant in consultation with the client prepares the contract documents; it checks the contractual documents and, if necessary, updates the written documents and plans in line with the variants selected and accepted by the client.

In the contract documents, the Consultant specifies the form, frequency, and dates for the submission of work progress reports by the contractors. It ensures that these requirements are met.

The Consultant will check the works contract(s) before they are signed by the company and the client, to confirm to the client that the contract documents comply with the Building Permit and the studies, and any variants approved by the client.

It assists the latter in signing the contract(s), countersigns them and receives a copy.

CONSTRUCTION SUPERVISION PHASE :

After signing of the construction works contract and upon commencement of the works, the consultant will receive the service order for the supervision phase and will have the following responsibilities.

GENERAL :

The Consultant manage and supervise the construction works and the various contractors ensuring that the project is executed the quality of works in accordance with state of art rules and agreed standards within allocated time and budget.

The consultant verifies compliance with the architectural, technical, and spatial provisions of the Works Contract. In this context, the Consultant must:

- Professionally manage, check and control any technical issue related to the construction   of Ruhengeri Referral hospital to ensure a successful completion of works.

- Check that the execution studies carried out by the Company comply with the provisions of the Works Contract(s) and the relevant design and standard documents and contain no errors, omissions or contradictions and, in this case, give its approval by "Visa" or, if not, have the Company draw up the rectifications necessary for unreserved approval of these studies before execution of the Works,

- Ensure that other documents produced by the Company comply with the provisions of the Works Contract(s), in particular as regards HQE (High Environmental Quality) or equivalent

- detect and report any non-compliance with the provisions of the Works Contract in the execution of the Works,

- Ensure that all materials and equipment allowed on the site are in full compliance with technical specification requirements and will certify the quality, if necessary, by means of tests and trials that are independent to those of the executive contractor.

- inform the Contractor before and as the work is carried out, of its refusal of defective materials and works or those that do not comply with the conditions of the Works Contract(s),

- take part in all technical and summary meetings, site meetings and visits, technical or economic meetings,

- give its opinion on prototypes, witnesses and material samples proposed by the company,

- inform the Contractor of any modifications envisaged, draw up its own recommendations and submit them to the client for approval prior to costing and execution of the work,

- draw up, during the course of the work, any documents (plans, details, technical instructions, etc.) complementary to the design studies that may prove necessary for a proper understanding of the works, it being understood that the execution plans and the implementation of the details are the responsibility of the Contractor,

- Amend detailed drawings as necessary and ensure prior approval from the client before they could be used for implementation.

- draw up all design elements relating to requests from the Client for modification or additional work, and

- Ensure that any new works deemed necessary to a good completion of the project and do not appear in the planned activities are duly quantified and their impact on the project identified and seek approval of the client before they are executed.

Obligations of the parties:

- the Consultant shall not make any changes to the design of the Project without the prior agreement of the client,

- The Consultant must advise the client on any technical changes proposed during execution and seek the client approval before their implementation.

- no additional work or modifications may be ordered by the Consultant without the prior agreement of the client, who signs the corresponding service order.

- the Consultant updates, whenever necessary, the entire file of plans appended to the Works Contract(s).

- The Consultant must immediately inform and advise the client of any contractor’s defect likely to harm the works both technically or/and financially.

- the Consultant refrains from issuing direct orders to contractors.

DURING STARTING PHASE OF CONTRACTOR’S WORK:

The consultant shall pay special attention to the following during the starting phase of the construction works:

- If the execution program and resources allocation proposed by the contractor for the execution of the project complies with acceptable and standard requirements to meet project objectives on time, in quality and cost effectively.

- The detailed project execution plan clearly detailing task milestones, resource allocation (both personnel and material) and key materials procurement plans shall be communicated to the client within a week after official start date. After which in collaboration all parties involved, the plan should be approved and make be part official project documentations.

- The qualifications and experience of the contractor staff to ensure they comply with the required expertise as specified in the contractor’s Terms of Reference.

- That the organization chart proposed by the contractor is adequate for smooth and professional completion of the project. The consultant will ensure to gather and communicate to the client the contact information (including phone numbers) of professional staff proposed by the contractor for the project.

- The availability, operational conditions of equipment brought by the contractor on the site and how they match with the tasks. Detailed update on this item shall be part of the weekly report mentioned above.

- Establish and maintain Project document control process in line with construction standards and the Project Delivery System (PDS) in order to ensure reliable and efficient administration, control, and distribution of information are in place.

VISAS OF CONTRACTORS' WORKING DRAWINGS:

The Consultant ensures that structural drawings are obtained in good time, checks them, validates them and forwards them to the contractors. An independent inspection agency as technical inspector's may be appointed to verify all stages of the project.

It arranges for all contractors to submit installation diagrams, plans and execution details (fittings, miscellaneous elements making up the structure, routes, hoppers, reserved sheaths, seals and miscellaneous details, etc.) and makes any necessary adjustments.

It summarizes them to ensure that the works are interdependent and in harmony with the project and arranges for the companies to make the necessary adjustments.

It ensures that these adjustments do not lead to any modification of the work, nor to an increase in the agreed prices, and that, where appropriate, they receive the agreement of the inspection office and/or the customer.

Within seven working days of receipt, it approves all execution documents and studies submitted by the company, after checking that they comply with the contract documents, the building permit and any amendments thereto, as well as current standards and Rwanda regulations (Rwanda Laws).

It constantly monitors the status of execution plan approvals by means of a summary table and ensures that no work is undertaken without these approvals and, where applicable, those of the technical controller.

The Consultant provide any missing design details that may be required by the contractor throughout the execution period.

It is specified that, unless otherwise agreed in writing by the client, the Consultant has a maximum of Seven (7) calendar days in which to issue the Companies with a response (approval with or without observations / justified refusal of approval) to the execution studies submitted to it, according to a document delivery schedule agreed between the Consultant and the Company, and in line with the provisional schedule for the Works approved by the client at the end of the Project studies.

In addition, the Consultant undertakes to respond to any proposals submitted by the Company within a maximum of fourteen (14) calendar days.

SUPERVISION OF WORK :

The Consultant controls the work and ensures that it is carried out, either by the general contractor or the contractors, in accordance with the plans drawn up, the approved specifications, the prescribed means of execution, and within the framework of the planned schedule.

In particular, it is responsible for the usable superstructure areas specified in the program: once the works have been completed, these areas, surveyed by the client's surveyor, must be within a "range" of plus or minus 2% (two percent) of those announced and agreed in the Contracts.

In the event of unforeseen circumstances, it will propose solutions to ensure that the work is carried out in accordance with the rules of the trade. In particular, it takes account of any opinions expressed by the designated inspection office, and carries out inspection visits at least once a week, and generally as often as necessary.

It ensures compliance with all legislative and regulatory requirements applicable to the work for which it is responsible. It refuses to lend itself to any operation that might infringe these regulations, prejudice the rights of third parties or lead to accidents.

It gives timely instructions and indications to ensure that work progresses according to the contractual schedule and the execution time limits provided for the project. The consultant endorses any request for extension of execution period and sent the request to the client for approval.

It Regularly provides technical advice to the contractor according to the needs.

It ensures that the criteria (materials, thickness, etc.) defined in the thermal study are respected at all stages of the project definition (detailed tender/consultation/works/acceptance of works).

In the event of a variant or a change in one of the criteria, a new thermal study is carried out to check that the objective remains unchanged.

With particular regard to the achievement of label and energy performance objectives, it imposes controls during construction and prior to acceptance of the works, to ensure that the quality of implementation enables the objective to be met, particularly with regard to HQE or equivalent.

It ensures that the project complies with the Contract throughout the construction phase, and to this end, it puts in place the necessary resources, in particular:

- product/equipment sheet approvals

- validation of samples / test areas / equipment

It proposes to the Client, for approval, the choice of harmonies and materials presented on samples by the Companies within the framework of the contract and, in general, all elements relating to the aesthetics of the building.

It provides all information and data needed to lift any reservations contained in the inspection office's and/or the customer's reports and undertakes to propose alternative solutions to the inspection office's remarks when these have an impact on the architectural appearance. It provides any information or element enabling the reservations to be lifted.

It makes recommendations to the client on all claims of the contractor relating to the execution and progress of the work, such as progress payments, variation orders, contract time extensions and suspensions, including interpretation of the contract between the client and the contractor.

It obtains the client's agreement on important decisions, in particular those concerning improvements and contingencies, so that these decisions can be implemented within a timeframe compatible with respect for the schedule.

It ensures that all technical query notes (TQN), Request for information, inspection and approval and Site Instructions (SI) are issued, checked, and submitted to the appropriate and right technical staff and properly registered and filed.

It maintains the document control system such that it is always up to date (daily) so that the client’s project manager and other relevant stakeholders has access to timely and accurate information, drawings, and documents.

It ensures that companies provide the Technical Controller with the samples and information needed to monitor manufacturing procedures and analyze the concrete produced.

Construction site meetings:

Throughout the project, and until all acceptance reservations have been lifted, the Consultant convenes and runs site meetings, weekly and additional special meetings it deems necessary, with the contractors. This meeting has the objectives to ensure that the work schedule is adhered to and notifies the client in the event of delays or early completion. The Consultant transmit the meeting outcomes to the client (RHA) in a written form and copy to Ruhengeri Referral Hospital and all those involved. The date of meeting should always be communicated to the client representatives assigned to the project for their potential attendance. The consultant will be responsible for preparing and sending invitations to concerned persons as well as to compile and transmit reports and/or related minutes at least two days before holding the next meeting. Progress documents drawn up by the Contractors are attached to these minutes.

Other meetings:

The Consultant takes part in the organization of all other appointments it deems necessary, and which would have an impact on the cost or completion date of the work, including partition visits (partitions completed, sockets and switches positioned, tiles laid, units cleaned), pre-delivery visits, delivery visits. To ensure that these appointments are properly carried out, she will issue any reminders and formal notices that may prove necessary, particularly with regard to the good state of finish of the units in relation to their stage of completion. The consultant is available on site during these appointments to provide any technical response to the Client.

Fine-tuning:

The Consultant draws up the sketches and plans required for the project to be completed to perfection: floor, wall and ceiling coverings where applicable, position of equipment and accessories in plan and elevation, etc., for approval by the client. In particular for validation by the Client.

Decision:

It decides, without delay, as work progresses, whether to reject defective materials and works or those that do not comply with the contracts.

It submits proposals for the selection of materials, supplies and equipment to the client in good time.

In particular, it organizes on-site meetings with contractors to enable the client to select materials, supplies and equipment. Prior to these meetings, it ensures that the proposed products comply with the standards, regulations and certifications applicable to the project. It draws up the minutes of these meetings for the attention of the client and the companies concerned.

Security:

The Consultant will be responsible for the security on the construction site. Indeed, the construction will be closed to an occupied and functioning hospital with a lot of passage. Thus the security of the construction site, of the materials and equipment’s, with the control of the personal on site is essential. In that regard, the Consultant will update the site logbook on daily basis.

The Consultant ensures that the contractor takes all necessary measures so that maximum security conditions for the workers and surrounding communities are observed and fulfilled.

Façade samples:

In due course, the Consultant invites the client, in the presence of the companies concerned, to any presentation of samples of the various facade materials (wall coverings, metalwork, wood, exterior joinery, etc.). It ensures that this presentation is made in situ and in sufficient dimensions to enable the client to make an informed choice. She prepares the minutes of these meetings for the client and the companies involved.

Presentation of interiors:

In due course, the Consultant invites the client, in the presence of the contractors, to any presentation of samples of the interiors to validate the choices before the order is placed. The Consultant ensures that the presentation is made in a situation and in sufficient dimensions to enable the client to make an informed choice. She draws up the minutes of these meetings for the attention of the client and the companies concerned.

Technical witnesses:

In due course, the Consultant invites the client, in the presence of the contractors, to any presentation of technical witnesses to validate the choices made before the order is placed. Minutes of these meetings are drawn up for the attention of the client and the companies concerned.

Quality control:

The Consultant collects and analyzes the companies' self-control documents.

It carries out periodic, scheduled site inspections: it inspects and examines the actual construction of the project with such frequency and duration as may be necessary to fully instruct the Contractor’s representatives on the work, the merits of the material and workmanship, and seeing to it that the work is strictly done in accordance with the plans and specifications. The Consultant shall keep the client informed of defects and deficiencies in the work of contractor and shall condemn work found failing to conform with the contract documents, Annexes or Special Provisions of the Construction Contract, if any, and decisions of the client as conveyed.

In order to limit rework at the end of the worksite, it carries out systematic quality controls on each room as the main phases progress:

- at least every two months during structural work,

- at water/air tightness,

- on completion of partitions/lining,

- after completion of tiles and earthenware,

- during pre-acceptance inspections.

Prior to the execution of the following phases, it gives the company the precise instructions required to obtain the quality corresponding to the work, deciding without delay, as the work progresses, to reject defective materials and works or those which do not conform to the contract.

These instructions are recorded in the form of inspection reports. A list of these reports is included in the minutes of weekly site meetings. It systematically checks the action taken on its instructions, which it repeats until the result is achieved.

Information from the client:

The Consultant keeps the client informed in writing of the quality of the work and the action taken by the companies in response to its observations.

In particular, it must draw up periodic reports for the client as mentioned in the paragraph under.

Progress report:

The Consultant sends progress certificates to the client without delay, so that he can make his calls for funds, in accordance with the stages of progress previously provided.

The Consultant must Submit to the client a weekly progress report comprising (but not limited to):

- The status of materials supplied and their compliance to agreed standards,

- Detailed description of works completed and ongoing activities,

- Problems encountered, and solutions proposed or taken,

- Progress of contract execution, approvals on invoice payments and financial report

At the end of each month, the Consultant also prepares and submit officially the monthly progress reports to RHA with copies to Ruhengeri Referral Hospital and the Rwanda Biomedical Center (RBC). This report should contain a statement of progress for each trade on the site at the end of the current month and, at the client's request, an estimate of technical progress at the end of the current year and the following year, it should also highlight actual and potential problems, need for urgent decisions, and likely deviations from overall quality, timing and costing plans.

Communications between the Consultant and the Contractor(s):

The Consultant Must Ensure that all the communications between the contractor and the consulting firm are officially recorded in a written form for future reference.

Additional work requested by the client:

Should the client decide, during the course of the project, to make changes that do not substantially alter the scope of the program, the Consultant may not, insofar as it cannot be held liable, oppose such requests, and must carry out any operations made necessary by such changes. The Consultant's mission includes:

- analysis of the client's requirements (advice on comfort of use, compliance with regulations, contract documents, building permits and any amendments, cost impact, integration into the schedule, compliance with labels and/or certifications, as well as with current standards and regulations,

- Updating of plans and specifications after approval by the client,

- monitoring and controlling the corresponding work.

The Consultant must submit to the client the request for Variation Orders that have been duly assessed and approved by a joint technical team.

The client transmits requests for modifications in summary form to avoid having to use excessive resources to take them into account.

BUDGETARY CONTROL:

The Consultant is also responsible for budgetary control during work execution:

- It keeps the client constantly informed of any financial claims made by contractors,

- It negotiates the financial and contractual implications with contractors before service orders are issued,

- It ensures that any modification to the contractual documents, whether or not involving a financial commitment, is the subject of an amendment to the contract.

In this context, no additional work by contractors will be remunerated without the prior written agreement of the client, on the proposal of the Consultant.

It prepares and approves service orders and amendments signed by the client.

It processes requests for additional work, from the request to the service order, within fourteen (14) days. It arranges for all the trades concerned to draw up the corresponding estimates, checks them (by checking quantities and unit prices, as well as verifying that the services are not provided for in the works contracts for one of the lots), submits them to the client for approval after analysis, draws up the appropriate amendments to the contracts, proposes the service orders for signature by the client, and manages the work within the scope of its mission.

It draws up a monthly summary table of amendments, indicating rejected estimates.

It thoroughly verifies the monthly statements of account proposed by the companies for payment by the Client; check their accuracy in conformity with the recommended model, countersign them after checking and if necessary, correct them and transit the approved invoice to the client with a clear recommendation of works completed and to be paid, within the agreed deadlines and in a single operation, the companies' statements of account accompanied by all supporting documents.

It may propose to the client the application of penalties in accordance with the terms of the contracts.

It keeps a monthly statistical and financial record of work undertaken.

It draws up payment certificates, including those for subcontractors eligible for direct payment.

The Consultant keeps the inter-company account up to date. It ensures that the terms of the Contract are properly applied, in particular with regard to the recovery of damage caused by one company to the works of another.

It accepts the principle that, if necessary, it will order the necessary work from the specialized companies of its choice - with priority given to site companies - on behalf and at the risk of the company concerned, and that in the event of a dispute between the companies, it will settle the matter between the parties.

To simplify account closure discussions, she makes contradictory observations backed up by photos whenever necessary. With these elements, she completes the file she keeps up to date as part of her budget monitoring. She makes all these elements available to the client.

It checks that these sums appear on the status reports.

It verifies briefs and draws up final accounts and checks payment certificates without assuming responsibility for the accuracy of calculations. It clears the final accounts at the end of the period specified in the Works Contracts. Final accounts will be drawn up by the Consultant in the event of default by a client.

In the event of faulty workmanship or faulty execution due to incorrect use of materials or use of defective materials, both during the course of the work and upon acceptance of the said work, the Consultant will assess whether such faulty workmanship should lead to total or partial repair of the work, or to a reduction in compensation, and will submit its proposal to the client for acceptance.

It presents the client with a monthly statement of financial commitments by company (contracts, amendments, amending service orders, etc.).

Prorata account: the Consultant is an ex-officio member of the Prorata Account Control Committee.

ADMINISTRATIVE MANAGEMENT OF CONTRACTORS AND SUBCONTRACTORS:

The Consultant must control administratively the contractors with the following objectives:

- Ensure that professionals employed on site by the contractor or sub-contractors comply with the required and agreed on expertise. For instance, ensuring that they are registered in their respective professional bodies if applicable, having insurance, appropriate contracts with the contractor and verify they credential to ensure they are relevant for the task to be executed.

- Ensure that the contractor takes necessary measures so that actions harmful to the environment are minimized as reasonably as possible and that possible repairs are carried out in due time.

The Consultant collects administrative and insurance documents from main contractors and subcontractors, with a view to their approval by the client. It forwards these documents to the client as and when they are obtained.

It ensures that the level of subcontracting is well limited with the agreement of the client to two ranks. In particular:

It undertakes in particular to collect from each company or person working on the site a certificate of insurance issued by their insurance company and approved by the insurer.

In the field of seconded labor, it will ensure that the companies concerned comply with the requirements of the French Labor Code or local equivalent , by keeping documents relating to seconded employees at the site office, the place where seconded employees work, as well as documents proving that these companies are carrying out a real and substantial activity in their country of establishment, all of which must be translated into French.

Similarly, in order to enable the client to exercise the control required of it by the French Labor Code, the Consultant will ensure that all companies, both for themselves and for their subcontractors, submit the following documents every six months until the end of their performance:

- A document stating their individual identification number assigned in application of the general tax code. If the co-contractor is not required to have such a number, a document stating its identity and address or, where applicable, the contact details of its tax representative.

- A document attesting to the regularity of the co-contractor's social situation a document issued by the body managing the compulsory social security scheme, stating that the co-contractor is up to date with his social security declarations and payment of the relevant contributions, or an equivalent document or, failing this, a certificate of provision of social security declarations and payment of social security contributions. In the latter case, the company must verify the authenticity of this certificate with the body responsible for collecting social security contributions.

Where registration of the co-contractor in a professional register is compulsory in the country of establishment or domicile:

- A document issued by the authorities holding the professional register or an equivalent document certifying this registration,

- A quotation, an advertising document or professional correspondence, provided that the name or corporate name, the full address and the nature of the entry in the professional register are mentioned.

For companies in the process of being set up, a document dated less than six months from the authority empowered to receive the entry in the professional register, attesting to the application for entry in the said register.

In the case of subcontractors, the documents must be produced on the day the subcontractor is presented for acceptance by the Consultant, and every six months from the date of acceptance and approval of the subcontractor's terms of payment.

The Consultant shall immediately notify the client in the event of any problem or failure to provide any of the documents in question.

The Consultant must update the site logbook on daily basis.

ASSISTANCE IN THE ACCEPTANCE OPERATIONS AND HANDOVER:

The Consultant will be involved in assisting the client in the technical and legal handing over process, guarantee and maintenance control, final payment, and preparation of the project completion report:

- the organization of operations prior to acceptance (provisional handover) of the works and delivery of the buildings, including visits to parts that will later become difficult to visit,

- instructions to contractors for their technical tests,

- functional technical OPRs (by sampling based on company self-checks),

- drawing up of the list of reservations formulated at the time of acceptance of work and delivery of buildings, drafting of pre-acceptance operation reports,

- prepare safety files for the safety commission,

- monitoring reservations until they are lifted and proposing acceptance,

- preparation of the file of executed work, including all documents required for the operation of the building, and

- examining any problems reported by the client during the perfect completion period.

Note: The supervisor Final report of the project after completion shall be submitted to the owner, within four (4) weeks after the provisional handover of the works.

Acceptance and removal of reservations:

Operations prior to acceptance:

With a view to and prior to acceptance of the works, the Consultant carries out pre-acceptance visits and ensures the coordination required for a smooth finish.

On this occasion, it draws up:

- a detailed list of reservations specific to each trade, i.e. any completion, finishing or repair work required,

- a methodology, recommendations, and prescriptions on the HQE targets implemented and their sustainability over time,

- the schedule for carrying out the work,

- It ensures that the work is carried out according to schedule.

In the event of a contractor's failure to perform, the Consultant proposes to the client any solutions that will enable the work to be completed on schedule.

On completion of the work, and with a view to the administrative declaration to be signed by the client, the Consultant certifies that the work complies with the building permit and, notwithstanding the acceptance operations, reconciles the drawings with the work carried out, and files the declaration of completion with the relevant authorities.

It also draws up all certificates attesting to the compliance of constructions with the legal and regulatory provisions in force, in particular those of the safety services.

It assists with inspection operations, and after agreement and signature by the client of the necessary service orders, directs, where appropriate, the execution of the work required to ensure compliance, for which it sets the deadline. It ensures that these operations are carried out promptly.

It carries all necessary steps to obtain the certificate of conformity.

The Consultant's mission ends at the latest of the following events: obtaining this certificate, signing all the final accounts, and lifting any reservations, including those covered by the guarantee of perfect completion.

Reception:

The Consultant assists the client in the reception of works.

In the presence of all duly convened contractors and the client or his representative, the Consultant, after examining the work and recognizing that it complies with the contract documents and has been implemented in accordance with the rules of the trade, proposes acceptance to the client; it draws up the minutes of acceptance of the work, mentioning any reservations noted.

It certifies that the building is fit for habitation (connections made, technical and safety equipment in working order, practical access, etc.).

It issues the necessary orders to the contractors to remedy any defects or shortcomings, specifying the deadlines set for them.

It directs and supervises the execution of repairs so that all reservations can be lifted within the allotted timeframe, i.e. 30 days maximum. In the event of default by a contractor, it sends formal notices to the companies, then proposes to the client all solutions enabling the reservations to be lifted.

Should these reservations not be lifted within the allotted time, the Consultant will provide the client with a summary table of the remaining reservations, item by item:

- the reservation and a summary description of the work to be carried out to remove the reservation,

- the cost of the work to be carried out in order to remove the reservation, by having an estimate drawn up by a third-party company capable of removing the reservations.

It also intervenes within the framework of the guarantee of perfect completion.

The Consultant assists the client, if the latter deems it necessary, during the handover operations.

It analyzes the reservations noted in the delivery reports. If it considers that a reservation cannot be accepted as such, it informs the client, justifying its position in writing.

The Consultant arranges for the issuance of the administrative certificates required for the acceptance of the installations by the public services or concessionaires or required by the inspection bodies.

It endorses the declaration of completion of the works, attaching the technical inspector's report that it has collected, and assists the client in obtaining the Certificates of Conformity, in liaison with the inspection bodies.

It draws up the as-built drawings (architect's plans).

The Consultant gathers and submits to the client before the final professional fees of the supervision:

- “As built plans” done by the contractor at the end of the project, verified and approved by the consultant. Three (3) sets of “as built plan” hard copy and soft copy on a pen-drive (flash-disks) should be transmitted to the client (RHA) and copy to RBC and Ruhengeri Referral Hospital. The plans should include architectural, structural, electrical, sanitary, mechanical and air-conditioning, Firefighting, Medical Gas layouts, Telecommunication, service- connected equipment, fixed furnishings and site planning work, all necessary for record purposes, building maintenance and repairs.

- Calculation notes, tests and trial results, measurements, contractor’s invoices, attachments and any other documents that may permit the proper interpretation and justification of all decisions about expenses incurred in course of the project,

- Documents required for the proper operation and maintenance of the works, drawn up by the designers, manufacturers, and equipment suppliers as part of their contractual obligations, as well as proposals for service and maintenance contracts and any documents included in the deeds of sale to purchasers,

- Workplace maintenance file,

- Certificate of compliance with current thermal regulations,

- Final report from the Technical Inspector with no reservations,

- All documents required to obtain the labels and certifications sought for the operation.

- A final report summarizing all the stages of project progress with comprehensive review of technical and financial aspects. This documentation must be accurate and show all the variations brought to the initial project and their justifications as well as the results in relation to the initial goals.

Completion work:

The Consultant must ensure that the following work is carried out quickly and diligently:

- Completion of the works before handover of the keys,

- Removal of reservations made during acceptance and delivery within the deadlines set during acceptance and delivery.

It takes the necessary measures to ensure that the client replaces any companies that fail to comply with this commitment, following formal notice.

It draws up all documents required for the removal of reservations noted during inspections, and checks that they have been fully complied with, within the deadlines set out in the contractual documents. In particular, it sets up a table for monitoring delivery reservations, which describes the reservation batch by batch and item by item, as well as a summary description of the work to be carried out to remove the reservation.

It collects releases from contractors and updates the table accordingly.

She completes the table of reservations at d+30, duly analyzed and accepted by him. If it considers that a reservation at d+30 cannot be accepted as such, it informs the client, justifying its position in writing.

Twice a week, it sends the Client an update of this table until all reservations have been lifted, supported by a discharge.

Once all the reservations have been removed, and the purchasers have given their discharge, the Consultant submits an amendment to the acceptance report for signature by the client, lifting all reservations.

TEAM COMPOSITION & QUALIFICATION REQUIREMENTS FOR THE KEY EXPERTS

The hospital project will encompass two distinct phases with unique requirements: a design phase and a construction phase. To meet the project's expectations throughout these two stages, the company must propose a tailored solution for each phase. This necessitates the formation of two distinct teams, with some specialized profiles potentially overlapping between the two project phases.

Design Phase:

- International Expertise: The design phase must adhere to stringent hospital standards for defining technical specifications. A team with prior hospital experience is crucial for this phase, as the upstream design stages are pivotal to the project's success.

- Senior Profiles: Senior-level professionals should be included in the design team to ensure the project's future success.

- Local collaboration

Technical Cooperation: Technical cooperation with a local team is essential to incorporate project-specific constraints, such as materials, construction methods, logistical considerations, and context integration.

Construction Phase:

- Local Supervision: A dedicated team must be permanently available on-site during the construction phase to ensure consistent and precise supervision.

- Support from Design Team: A support from the design team is recommended to maintain continuity throughout the project, leveraging their specialized hospital experience.

Team Composition:

- Distinct Teams: To address these organizational requirements, team composition should be divided into design and supervision roles, each with specialized profiles.

- Profile Overlap: However, the company may propose the same profiles for both phases if the technical lead possesses the necessary expertise across all criteria.

Additional Considerations:

- Clear Roles and Responsibilities: Clearly define the roles and responsibilities of each team member to ensure seamless collaboration and avoid task duplication.

- Effective Communication: Establish effective communication channels between the design and supervision teams to facilitate information exchange and maintain project alignment.

- Continuous Monitoring: Implement a continuous monitoring system to track progress, identify potential issues early on, and take corrective actions as needed.

For the profile of proposed personnel, the consultancy firm must provide the following:

- The copy of the degree

- Signed and updated Curriculum Vitae (CV) of the concerned staff with their contract telephones and emails.

Please be advised that the information provided in this document is subject to change without notice.

- The supporting documents must be very clear and reliable as they may be used in case of need of verification.

- A staff without the required degree will lose all the marks for the position he/she is proposed.

- The CVs of all personnel shall be submitted during the Bid submission as there may be requested when and as required during the implementation of the assignment for the successful bidder.

- Without prejudice of the provisions of the laws and regulations governing public procurement, no document shall be accepted by the Procuring Entity after bid opening.

- Reimbursable and Miscellaneous Expenses if applicable, must be paid upon submission of proofs and supporting documents by consultant.

- The candidates who are black listed are not eligible (Each candidate will undergo a check of UN, EU, France and World Bank financial sanctions lists).

- The local Consulting Firms registered in Rwanda should be classified under Category A in building supervision services. However, a non-categorized foreign company is allowed to bid for this tender but before contract signature, a non-categorized foreign company must provide proof of application for categorization to the state organ in charge of public procurement (Rwanda Public Procurement Authority) certifying that the organ has received the request for categorization."

- Foreign consulting firm entering into JV agreement with a local consulting firm, the local consulting firm must be classified under Category A in building supervision services.

- The Applicant shall submit only one application, either in its own name or as a member of a Joint Venture (JV). If an Applicant (including any JV member) submits or participates in more than one application, those applications shall be all rejected.

- If the Applicant is a JV, the applicant shall submit:

  - JV for international companies only:

- A notified copy of the JV Agreement signed by both parties entered into by all members,(In the absence of this document, the bid will be rejected) .

  - JV with For local companies

- JV agreement is evidenced by an agreement signed before the notary of the organ in charge of registration of companies (Rwanda Development Board).

By adhering to these recommendations, the company can effectively manage the project's two distinct phases, ensuring both technical excellence and operational efficiency.

PROFILE OF THE SUPERVISING FIRM

The firm must be registered in the E-procurement system in Rwanda at umucyo.gov.rw.

The company should be a consulting firms and have general knowledge in detailed design and supervision of construction project.

The supervising firm should be registered for practicing which shall be proven by the certificate of Company registration.

PROFILE OF THE DESIGN TEAM

The Consultant undertakes to put in place the human and material resources required by the nature and scale of the Project for the proper performance of its obligations hereunder.

The design team must possess international expertise in hospital engineering, demonstrating the ability to adapt to the local context while adhering to international standards. The company should prioritize candidates with extensive hospital experience. The detailed profiles and specific competency expectations for each professional are outlined below. However, it is important to note that this list is not exhaustive and may be supplemented or enhanced based on the company's available talent pool. Careful selection is crucial to ensure the successful execution of this demanding project with high-caliber clients.

Key Requirements:

- International Hospital Engineering Expertise: Proven experience in designing and implementing hospital facilities that meet international standards and best practices.

- Adaptability to Local Context: Demonstrated ability to understand and incorporate local regulations, construction practices, and cultural considerations into project design.

Additional Considerations:

- Project Management Expertise: Ensure the design team includes experienced project managers to oversee planning, scheduling, budgeting, and risk management.

- Communication and Collaboration Skills: Foster a collaborative environment within the design team and with other project stakeholders to ensure effective communication and coordination.

- Client Relationship Management: Assign a dedicated client relationship manager to maintain open communication with clients, address their concerns, and manage expectations throughout the project.

To this end, the Consultant has put together a team of qualified English-speaking professionals under the direction of a Project Manager. :

| Reference | Staff name | Qualification | Number | General experience | Specific experience | Man-Months for design phase |
| --- | --- | --- | --- | --- | --- | --- |
| K1 | Team Leader – Design Manager | Bachelor’s Degree in Civil Engineering, or Architecture | 1 | A minimum of ten (10) years of experience leading or participating in international projects of similar scope. | At least three (3) Hospital Design Project for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€ each) proven by signed CV. | 9 months |
| K2 | Senior Architect | Bachelor’s Degree in Architecture | 1 | A minimum of eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) Hospital design Project for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€ each) proven by signed CV. | 9 months |
| K3 | Architect | Bachelor’s Degree in Architecture | 3 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (1) Hospital design Project for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€) proven by signed CV. | 9 months |
| K4 | Senior Structure Engineer | Bachelor’s Degree in Civil Engineering or Structural Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) Hospital design Projects in construction management and/or infrastructure (of at least 10 M€) proven by signed CV | 9 months |
| K5 | Structure Engineer | Bachelor’s Degree in Civil Engineering or Structural Engineering | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (1) Hospital design Project for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€) facility. Experience in completing projects from design to commissioning proven by signed CV | 9 months |
| K6 | Senior Water Sanitation and Hygiene Engineer | Bachelor’s Degree in Water, Sanitation, and Hygiene Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least 3 projects related to Water, Sanitation, and Hygiene (WASH), plumbing, sanitation, and solid and liquid waste management in a healthcare facility. Experience in completing projects from design to commissioning proven by signed CV | 9 months |
| K7 | Senior Electrical Engineer | Bachelor’s Degree in Electrical Engineering, Electrical Power Engineering or Electrical and Electronics Engineering (Option Electrical): | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) projects related to electrical systems including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.). Strong IT and Computer Engineering expertise is required to implement network and low-current technical installations proven by signed CV | 9 months |
| K8 | Electrical and Electronics Engineer | Bachelor’s Degree in Electrical and Electronics Engineering | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (1) project related to electrical and Electronics systems comparable to those of hospital, including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.). Experience in managing projects from design to commissioning proven by signed CV. | 9 months |
| K9 | Senior Mechanical Engineer | Bachelor’s Degree in Mechanical or Electromechanical Engineering | 1 | A minimum of ten (10) years of experience leading or participating in international projects of similar scope. | At least 3 projects related to fluids and air conditioning in the hospital including: Medical Gases, HVAC, plumbing, water treatment successful completion of projects from design to commissioning will be highly valued. Experience in the laboratory sector will also be considered an asset. proven by signed CV | 9 months |
| K10 | Mechanical Engineer | Bachelor’s Degree in Mechanical or Electromechanical Engineering | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (1) hospital fluid project with technical facilities (including Multi-fluid: Medical Gases, HVAC, plumbing, water treatment operating rooms) of the same scale proven by signed CV | 9 months |
| K11 | Senior Biomedical Engineer | Bachelor’s Degree in Biomedical Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) hospital projects with the same level of technical facilities, supply, and installation projects for hospital equipment, including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.) and a medical biology laboratory. Experience in completing projects from start to finish (including commissioning of equipment) and providing maintenance plans for the equipment. proven by signed CV | 9 months |
| K12 | Biomedical Engineer | Bachelor’s Degree in Biomedical Engineering | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (1) hospital projects with the same level of technical facilities, supply, and installation projects for hospital equipment, including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.) and a medical biology laboratory. proven by signed CV | 9 months |
| K13 | Senior Environmental Quality Consultant | Bachelor’s Degree in Environmental Sciences, Environmental Studies, Environmental Management, Environmental Engineering or Environmental Technology | 1 | At least Eight (8) years of experience in project management support for energy efficiency and environmental certification of hospitals. | At least three (03) environmental and social impact projects in the field of hospital or civil engineering projects proven by signed CV | 9 months |
| K14 | Topographic Surveyor | Bachelor’s Degree in Geography, GIS, Surveying and Geomatics Engineering, Land Surveying or Topographic Surveying. | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one building construction projects encompassing either project study/design or supervision proven by signed CV | 9 months |
| K15 | Senior Geotechnical Engineer | Bachelor’s Degree in Geotechnical Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) building construction projects encompassing either project study/design proven by signed CV | 9 months |
| K16 | Senior Quantity Surveyor | Bachelor’s degree in Quantity Surveying, Construction Economics or Building Economics | 1 | At least eight (8) years' experience, with experience in similar projects in the export sector desirable. | At least three (3) hospital projects proven by signed CV | 9 months |
| K17 | IT Systems Engineer | Bachelor Degree in Informatics, Computer Engineering | 1 | At least four (4) years' experience, with experience in similar projects in the export sector desirable. | At least one (1) project related to IT systems and communication systems comparable to those of hospital, including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.). Experience in managing projects from design to commissioning proven by signed CV. | 9 months |

- Man Month provided herewith will be basis for evaluation of financial proposals.

- The bidders are not allowed to change the Man Months provided in the tender document.

PROFILE OF THE SUPERVISION TEAM

The Consultant undertakes to put in place the human and material resources required by the nature and scale of the Project for the proper performance of its obligations hereunder. To this end, the Consultant has put together a team of qualified English-speaking professionals under the direction of a Project Manager. :

The supervision team must have a dedicated local team permanently available on-site to ensure close monitoring of the construction contractors for the future hospital project. Due to the project's complexity, particularly with a phased approach, occupied site, and ongoing service operations, it is recommended to have professionals with prior experience in renovation projects, preferably in a hospital setting. The technical nature of the project calls for experienced engineers with significant construction site supervision experience, particularly in disciplines such as electrical, HVAC, and plumbing.

Key Requirements:

- Dedicated Local Team: A permanent local team must be present on-site to provide continuous monitoring of construction activities and ensure adherence to project plans, specifications, and quality standards.

- Renovation Project Experience: Professionals with prior experience in renovation projects, particularly in a hospital setting, are highly preferred. This experience will be invaluable in navigating the complexities of working in an occupied site while maintaining ongoing service operations.

- Technical Expertise: The supervision team should include experienced engineers with significant construction site supervision experience, particularly in disciplines such as electrical, HVAC, and plumbing. This expertise will be crucial in ensuring the proper installation and commissioning of complex building systems.

Additional Considerations:

- Project Management Expertise: Ensure the design team includes experienced project managers to oversee planning, scheduling, budgeting, and risk management.

- Communication and Collaboration Skills: Foster a collaborative environment within the design team and with other project stakeholders to ensure effective communication and coordination.

- Client Relationship Management: Assign a dedicated client relationship manager to maintain open communication with clients, address their concerns, and manage expectations throughout the project.

| Reference | Staff name | Qualification | Number | General experience | Specific experience | Man-Months for supervision phase |
| --- | --- | --- | --- | --- | --- | --- |
| K1 | Team Leader - Construction Manager | Bachelor’s Degree in Civil Engineering, or Architecture | 1 | A minimum of ten (10) years of experience leading or participating in international projects of similar scope. | At least three (3) Hospital Supervision Projects for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€ each) proven by signed CV | 25 months |
| K2 | Senior Architect | Bachelor’s Degree in Architecture | 1 | A minimum of eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) Hospital Supervision Projects for construction and/or rehabilitation projects in the realization of hospital infrastructure and equipment projects (of at least 10 M€ each) proven by signed CV | 25 months |
| K3 | Senior Structure Engineer | Bachelor’s Degree in Civil Engineering or Structural Engineer | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) projects in hospital construction management and/or infrastructure supervision proven by signed CV | 25 months |
| K4 | Water Sanitation and Hygiene Engineer | Bachelor’s Degree in Water, Sanitation, and Hygiene Engineer | 1 | A minimum of Four (4) years of experience leading or participating in international projects of similar scope. | At least 1 Supervision project related to Water, Sanitation, and Hygiene (WASH), plumbing, sanitation, and solid and liquid waste management in a healthcare facility proven by signed CV | 25 months |
| K5 | Senior Electrical Engineer | Bachelor’s Degree in Electrical Engineering, Electrical Power Engineering or Electrical and Electronics Engineering (Option Electrical): | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) Supervision projects related to electrical systems including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.). Strong IT and Computer Engineering expertise is required to implement network and low-current technical installations proven by signed CV. | 25 months |
| K6 | Senior Mechanical Engineer | Bachelor’s Degree in Mechanical or Electromechanical Engineering | 1 | A minimum of ten (10) years of experience leading or participating in international projects of similar scope. | At least 3 Supervision projects related to fluids and air conditioning in the hospital including: Medical Gases, HVAC, plumbing, water treatment successful completion of projects from design to commissioning will be highly valued. Experience in the laboratory sector will also be considered an asset. proven by signed CV | 25 months |
| K7 | Mechanical Engineer | Bachelor’s Degree in Mechanical or Electromechanical Engineering | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (01) hospital Supervision projects as Fluid with technical facilities (including Multi-fluid: Medical Gases, HVAC, plumbing, water treatment operating rooms) of the same scale proven by signed CV | 25 months |
| K8 | Senior Biomedical Engineer | Bachelor’s Degree in Biomedical Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (03) hospital Projects of technical facilities, supply, and installation projects for hospital equipment, including an imaging and interventional technical platform (operating room, emergency department, intensive care unit, etc.) and a medical biology laboratory. Experience in completing projects from start to finish (including commissioning of equipment) and providing maintenance plans for the equipment proven by signed CV | 25 months |
| K9 | Senior Quantity Surveyor | Bachelor’s degree in Quantity Surveying, Construction Economics or Building Economics | 1 | At least eight (8) years' experience, with experience in similar projects in the export sector desirable. | At least three (03) projects in construction management and/or supervision proven by signed CV | 25 months |
| K10 | Quantity Surveyor | Bachelor’s degree in Quantity Surveying, Construction Economics or Building Economics | 1 | A minimum of four (4) years of experience leading or participating in international projects of similar scope. | At least one (01) project in construction management and/or supervision proven by signed CV | 25 months |
| K11 | Health, Safety, and Environment Engineer | Bachelor’ Degree in HSE (Health, Safety, and Environment), QHSE (Quality, Health, Safety, and Environment) or Civil Engineer. | 1 | At least four (4) years of experience in construction site health and safety. | At least one (1) years of experience in health and safety monitoring for construction/rehabilitation projects of hospitals, healthcare facilities, or similar infrastructure, particularly in Africa context proven by signed CV | 25 months |
| K12 | Senior Environmental Quality Consultant | Bachelor’s Degree in Environmental Sciences, Environmental Studies, Environmental Management, Environmental Engineering or Environmental Technology | 1 | At least Eight (8) years of experience in project management support for energy efficiency and environmental certification of hospitals. | At least three (03) environmental and social impact projects in the field of civil engineering proven by signed CV | 25 months |
| K13 | Senior Geotechnical Engineer | Bachelor’s Degree in Geotechnical Engineering | 1 | A minimum of Eight (8) years of experience leading or participating in international projects of similar scope. | At least three (3) building construction project in supervision proven by signed CV | 25 months |

The Consultant and the Client mutually undertake to seek the best possible cooperation between the Consultant team and the project owner's representatives.

In consideration of the importance of the Project, its complexity, and its duration, it is hereby emphasized the importance attached to maintaining the team put together by the Project Manager for the needs of the Project during its whole course. Consequently, the project manager will inform the Client in advance of any temporary or permanent replacement of the project manager that may become necessary during the contract. The Client reserves the right to request the replacement of the new contacts thus designated by the Consultant.

The Consultant may be assisted by any other parties (specialized engineering firms, consultants, etc.) that it deems useful to appoint as part of its tasks (in addition to those already appointed or to be appointed by the project owner), and which it will be responsible for paying, it being specified that the Consultant will remain solely responsible to the project owner. These parties must have been accepted in advance by the project owner.

DURATION OF SERVICES:

The assignment for complete detailed design for rehabilitation of Ruhengeri Referral Hospital shall be done within months as illustrated in the table below:

| Phase | Timelime for submission |
| --- | --- |
| Inception Report & Sketch Studies | Two months including the validation period (i.e 6 weeks for production and submission of the report + 2 weeks for client’s validation). The consultant will be allowed two weeks for addressing the comments and Finalization of the report) after the receipt of service order for commencement of the study |
| Preliminary Design | Two Months Including the validation period (i.e 6 weeks for production and submission of the report after approval of the Inception Report & Sketch Studies + 2 weeks for client’s validation. The consultant will be allowed two weeks for addressing the comments and Finalization of the report) after approval of the Inception Report & Sketch Studies |
| Detailed Design | Four months including the validation period (i.e 3 months of Detailed Design production after approval of the Preliminary Design + One month for client’s validation. The consultant will be allowed two weeks for addressing the comments and Finalization of the report |
| Final Report : - Construction Document - Tender Documents | One Month after approval of the Detailed Design (Including One week for Client’s validation) |

The duration of each report includes its validation period, means the report will be submitted in advance prior to its approval as indicated.

The supervision of work will last the entire period of the rehabilitation works which is estimated to 25 months (Twenty-Four (24) months for construction plus one (1) month for production of final report).

INFORMATION PROVIDED BY THE CLIENT AND FOLLOW UP OF THE PROJECT:

The client shall put at the disposal of the consultant all the relevant documents and data concerning the conceptual model illustrating the client requirements. The consultant will receive a complete set of feasibility study comprising the needs assessment made of the following documents (as well as the one described in the Data Sheets ITC 2.4):

- The “functional program” which describes in detail the organization and functionality of each space or service within the hospital and also proposes feasibility on the site and environmental requirements.

- The “technical program” specifies the detailed technical characteristics and/or expected performances concerning the organization and design of the hospital project, as well as a detailed equipment plan.

- The “Detailed data sheets” for each room are included in a separate volume. They are published space by space, with all architectural and technical features, as well as medical equipment and furnishings.

- The “bioclimatic and environmental program” specifies the detailed bioclimatic and environmental characteristics and/or expected performances concerning the organization and design of the hospital project.

- The “Gender Action Plan”

- The “Table of deliverables” specifies the list of deliverables expected during the various phase of services. This list is not exhausted.

The client will assign a representative to be the focal person for the duration of the project.

The client will provide all administrative documentation such access passes and recommendation letter that might be need to facilitate the consultants in execution their assignments.

The consultant has a responsibility to reserve a section in his report to explain who they catered for the information and data provided by the consultant either by using them or disregarding them.

The provision of some information from the client to the consultant does not waive from the consultant his responsibilities to check the robustness and accuracy of the information prior their use.

In the project reports the consultant will reserve a section explaining how they considered the information provided by the client and/or reasons for disregarding them if they decided to do so.

The client reserves the right to amend any information or instruction provided in the documents shared to the consultant if found necessary for the sake of the smooth and possible implementation of the project

Terms of Reference - Security

- Preamble

The Consultant must show the care it exercises to protect its employees who perform Works in the country. Therefore, it must identify the risks and, in light of this analysis, define prevention and protection resources, incorporating additional resources therein, which may be organisational, technical or human resources. These elements shall be described in a methodology, which for each of the headings below must address and describe what the Consultant has planned.

Disclaimers:

1 - 	Although the specified admissibility requirements endeavour to correlate with the potential risks to which the Contract may be exposed, they are intended to be used solely to evaluate Proposals in order to eliminate Proposals that do not meet a minimum set of requirements. They are in no event to be understood to constitute sufficient measures to ensure the security of persons and property in connection with the Contract. The risk assessment and security measures to be defined in consequence thereof are the responsibility of the Consultant, who shall explain them in its security methodology.

2 - 	A methodology that fails to meet any one of the admissibility requirements set out in the sections below will be declared non-compliant and the Proposal of the Consultant will be rejected.

- Analysis of security issues and threats

The Consultant shall describe its view of the security environment and threats in the area where the Contract will be performed and/or the danger area, and present a security analysis for the relevant area and for the activities it will perform therein. It shall specify the method and references used to perform this analysis and describe the main threat scenarios that can be identified at the Proposal stage.

In addition, it shall at all times be able to share information learned from its country watch by its local organisation or head office.

Admissibility requirements: - Document describing the method used to carry out this analysis; - At least one identifiable reference source must be used; - Identification and evaluation of security threats in relation to the contract;

- General security organisation

The Consultant shall define the general security roles and responsibilities within its organisation and the allocation of the associated tasks for this Contract (including subcontractors and co-contractors), and shall designate a security reference person. It shall define the planned organisation and resources. In the event of a Joint Venture (JV), the leader shall designate a security officer as the JV’s sole contact for this Contract.

Admissibility requirements: - Description of the organisation; - The Consultant (and each member in the case of a JV) shall provide the name of the company’s internal security officer, who shall be responsible for defining and monitoring the measures implemented for the Contract.

- Specific security measures planned

Based on its own security analysis and the main threat scenarios it may have identified, the Consultant shall plan specific and appropriate measures. These measures shall cover at least the following matters:

4.1	Security organisation

The Consultant shall describe its local security organisation in the country where the Services will be performed. In particular, it shall specify whether this organisation relies on internal resources, using its own resources already existing in the country, or whether it uses a local partner, a security services provider or a "Security Officer" dedicated to the Contract, or whether it relies on the country’s State resources and whether it can request them directly. It shall describe the respective roles planned for each participant operating locally.

Admissibility requirements: - Description of the organisation and resources mobilised in the country of the Contract; - The Consultant (and each member in the case of a JV) shall provide the name of the person who will be its contact for all security issues in relation to the Contract. This person may be the same person identified in Article 3 above; - In the event of a JV, describe the coordination and distribution of responsibilities among the members;

  - Travel within the country and to the relevant area

Depending on the security analysis, special measures may be required to ensure secure travel within the country. These means may include the use of aircraft of national companies or private aircraft, the use of passenger vehicles, or maritime or inland waterways.

The Consultant shall describe the resources and measures planned to protect itself against security risks (crime, kidnapping, etc.) during these trips. These provisions may be technical, organisational or human. It shall distinguish between measures concerning protective actions and measures deemed forward-looking actions.

The Consultant shall describe the planned transport logistics, including human, technical and organisational resources and mechanisms for monitoring travel. It shall also define its requirements for maintenance management and rules of conduct.

Admissibility requirements: - Description of modes of travel, the physical means of travel and the security measures planned in connection with such travel; - Distribution of roles and measures planned for the Consultant itself, for external participants and those expected from the Client and local authorities, identifying each actor;

  - Accommodation during assignments

If the accommodation and security measures of the Consultant are not provided by the Client or the works company (in the case of construction project), the Consultant shall describe the type of accommodation and the measures planned to ensure the security of teams (security guards, physical means, etc.).

Admissibility requirements: - Description of the accommodation selection criteria and security measures planned for each overnight stay; - Provision of the names and addresses of hotels or accommodation venues planned for overnight stays;

  - Communication

The Consultant shall implement a communication and exchange process between the various Contract participants, to ensure reporting of security events, and that preventive or corrective actions deemed necessary are properly carried out. It shall describe the means enabling it to ensure effective communication.

Admissibility requirements: - Description of the planned means of communication and measures taken to ensure their reliability;

- Information, awareness-raising and training before departure

The Consultant shall make arrangements to inform, raise awareness and train its employees prior to departure on assignment. These arrangements shall be in the form of formal communication actions. It shall describe the provisions specifically planned for this Contract, in the form of "service orders" or similar documents.

Admissibility requirements: - Description of essential instructions provided to employees (welcoming, briefings, updating of instructions booklets, etc.); - Provision of the list of emergency numbers (local numbers and service providers, repatriation, head office on-call security service) furnished for the Contract’s assignments;

- Alert management and crisis management

The Consultant shall prove that it has set up a crisis management process involving the local organisation and its head office. It shall describe the main procedures for triggering this process and its key operating procedures.

For this purpose, the Consultant shall describe the alert process, from the local organisation to its head office, and the interaction with the Client.

Admissibility requirements: - Summary of the crisis management procedure dedicated to security, describing triggers, roles and responsibilities.