## cover page-
PROJECT:- REHABILITATION OF ABA'ALA GENERAL HOSPITAL
GENERATOR SUPPLY, INSTALLATION AND ANCILLARY WORKS FOR ABA’ALA HOSPITAL - 24-MR9564
LOCATION: - ABA'ALA ,AFAR, ETHIOPIA
January 2025

## Grand Summ
Project :-Rehabilitation of Abala Primary Hospital
Owner:- Abala Primary Hospital
Location:- Aba'ala, Afar, Ethiopia
Implementer : -Expertise France Groupe AFD
Contractor:-
Generator supply, installation, and ancillary works for Aba’ala Primary Hospital
Item no. | Description of works | Amount (Euro)
1 | MAIN DISTRIBUTION BAORD - CMDB | 0
2 | BLOCK-LABARATORY | 0
3 | BLOCK-OPERATION THEATER | 0
4 | ATS (Automatic Transfer Switch) | 0
5 | POWER CABLE | 0
6 | GROUNDING SYSTEM | 0
7 | GENERATOR | 0
| Total | 0
| REBATE (%) | %
| TOTAL AFTER REBATE | #VALUE!
| Vat (15 %) | #VALUE!
| GRAND TOTAL | #VALUE!

## BoQ
Project :-Rehabilitation of Abala Primary Hospital - Contract 24-MR9564
Location:- Aba'ala, Afar, Ethiopia
Implementer : -Expertise France Groupe AFD
Contractor:-
Generator supply, installation, and ancillary works for Aba’ala Primary Hospital
| Item no | Description | Unit | Qty | Rate | Amount | Remark
Note :- All distribution boards , breakers , switches, accessories etc. should be genuine Legrand or approved equivalents complying with IEC standards. Distribution boards should be made of sheet metal and have separate neutral and ground busbars/phase bars. All units in the distribution boards should be labelled to give the reference and duty of the unit. All fittings are subjected to owners approval, based on samples, catalogues presented by contractor. Unit price shall include all the necessary assistance civil works such as chiselling of walls, floors, beams, terrazzo, excavation, and etc. and replacing the terrazzo, re-plaster to fine finish, applying of approved type paint, etc.
| 1 | Main Distribution board CMDB
| 1.1 | CMDB-1 | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and verminproof, cubical type, bottom /top entry, free standing with following incoming and outgoing on floor with the help of nut &bolts and as per standard practice. Floor standing board The panel must be fabricated with 14/16 gauge MS sheet having two coats of red oxide & gray paint. The panel must include - Digital Energy Multimeter type PM210 with CTs and fuse protection; for indication of voltage, current, KW, KWh, KVA, Power Factor, frequency, etc( with 3x 300A/5 Current transformers for each phase) - Bus bar: for each phases and also One piece for grounding and one for neutral can hold the main load capacity(Bus-bar Capacity 400A hard drawn copper bus- bars, 3P+N) - AC load with 380v/400v 300A with main switch gear, Fuse, bus bar, surge protection device 40Ka with appropriate isolation MCB rated 32 Amps 3 phase - Cabinet dimension= can propose appropriate dimension N.B the board needs foundation/standing structure (Price shall include)
1X MCCB 300A 35 KA Incoming
1X MCCB 200A 35 KA 3 Ph
1X MCCB 125A 25 KA 3 Ph
1X MCB 50A 6KA 3 Ph (spare)
1X MCB 32A 6KA 3 Ph (spare)
|  | Carried to Summary |  |  |  | 0
| 2 | BLOCK-LABARATORY
| 2.1 | MDB XRAY | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and vermin proof, cubical type, bottom /top entry, compartmentalized (sectioned) -The panel must be fabricated with 14/16 gauge MS sheet having two coats of powder paint The panel must include -Bus bar/Distribution compact busbar/phase bar for balanced distribution of phases COMPLETE WITH DIN RAIL, NEUTRAL AND EARTH TERMINALS, with 25% free space - Cabinet Dimension ( can propose appropriate dimension )
1X MCCB 125A 25 KA Incomming
1X MCB 32A 6KA 3 Ph
1X MCB 40A 6KA 3 Ph
1X MCB 16A 10KA 1 Ph
1X MCB 20A 10KA 1 Ph
11X MCB 16A 6KA 1 Ph
1X MCB 16A 6KA 1 Ph( Spare)
1X MCB 10A 6KA 1 Ph( Spare)
| 2.2 | SDB LAB | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and vermin proof, cubical type, bottom /top entry, compartmentalized (sectioned) -The panel must be fabricated with 14/16 gauge MS sheet having two coats of powder paint The panel must include -Bus bar/Distribution compact busbar/phase bar for balanced distribution of phases COMPLETE WITH DIN RAIL, NEUTRAL AND EARTH TERMINALS, with 25% free space - Cabinet Dimension ( can propose appropriate dimension )
1X MCB 40A 6 KA Incomming
5X MCB 10A 6KA 1 Ph
4X MCB 16A 6KA 1 Ph
1X MCB 10A 6KA 1 Ph( Spare)
1X MCB 16A 6KA 1 Ph( Spare)
| 2.3 | SDB ADMIN | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and vermin proof, cubical type, bottom /top entry, compartmentalized (sectioned) -The panel must be fabricated with 14/16 gauge MS sheet having two coats of powder paint The panel must include -Bus bar/Distribution compact busbar/phase bar for balanced distribution of phases COMPLETE WITH DIN RAIL, NEUTRAL AND EARTH TERMINALS, with 25% free space - Cabinet Dimension ( can propose appropriate dimension )
1X MCB 25A 6 KA Incomming
2X MCB 10A 6KA 1 Ph
3X MCB 16A 6KA 1 Ph
1X MCB 10A 6KA 1 Ph( Spare)
1X MCB 16A 6KA 1 Ph( Spare)
|  | Carried to Summary |  |  |  | 0
| 3 | BLOCK-OPERATION THEATER
| 3.1 | MDB OPR | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and vermin proof, cubical type, bottom /top entry, compartmentalized (sectioned) -The panel must be fabricated with 14/16 gauge MS sheet having two coats of powder paint The panel must include -Bus bar/Distribution compact busbar/phase bar for balanced distribution of phases COMPLETE WITH DIN RAIL, NEUTRAL AND EARTH TERMINALS, with 25% free space - Cabinet Dimension ( can propose appropriate dimension )
1X MCCB 200A 35 KA Incomming
1X MCB 40A 6KA 3 Ph
1X MCB 63A 10KA 3 Ph
1X MCB 63A 6KA 1 Ph
1X MCB 20A 6KA 1 Ph
12X MCB 16A 6KA 1 Ph
1X MCB 16A 6KA 1 Ph( Spare)
1X MCB 10A 6KA 1 Ph( Spare)
| 3.2 | SDB OPR | Pcs | 1 |  | 0
Supply & installation of sheet steel fabricated dust and vermin proof, cubical type, bottom /top entry, compartmentalized (sectioned) -The panel must be fabricated with 14/16 gauge MS sheet having two coats of powder paint The panel must include -Bus bar/Distribution compact busbar/phase bar for balanced distribution of phases COMPLETE WITH DIN RAIL, NEUTRAL AND EARTH TERMINALS, with 25% free space - Cabinet Dimension ( can propose appropriate dimension )
1X MCB 40A 6 KA Incomming
4X MCB 10A 6KA 1 Ph
7X MCB 16A 6KA 1 Ph
1X MCB 10A 6KA 1 Ph( Spare)
1X MCB 16A 6KA 1 Ph( Spare)
|  | Carried to Summary |  |  |  | 0
| 4 | ATS
| 4.1 | ATS1 | Pcs | 1 |  | 0
Supply, Installation and Commssinoing of Automatic Transfer Switch (ATS ) Pannel Board in sheet steel enclosure with lockable door, and consisting of :- •Floor Standing Board •500A rated bus bar rated bus bar for incoming and outgoing Connection •Fully Automatic and Motorized 400Amp , 4 pole Automatic Transfer Switch With manual optional operation •1x400 A MCCB for mains incommer •Indication for each bus power with required Control Components & protective devices for it to be controlled by the Genset controller, which must include mains and generator close relays with iterlocks •Suitable for out door Installation/ inside on open Shed •25% free Spaces N.B the board needs foundation/standing structure
| 14 | Modular UPS 100KW scalable to 300KW, 400V w/Integrated Modular Distribution |  | Pcs | 1
Output
Output power capacity:100K Watts
Number of power modules:N+1
Capacity of each power module:Please specify
Nominal Output Voltage:230V, 400V 3PH
Output Voltage Note:Configurable for 380 : 400 or 415V 3 Phase nominal output voltage
Efficiency at Full Load:0.95
Output Voltage Distortion:Less than 2%
Output Frequency (sync to mains):50/60 Hz +/- 3 Hz user adjustable +/- 0.1
Output Frequency (not synced):50Hz +/- 0.1% for 50Hz nominal
Topology:Double Conversion Online
Waveform type:Sine wave
Overload Operation:10 minutes @125% and 60 seconds @150%
Output Voltage THD:< 2% for 0 to 100% linear load and < 6% for full nonlinear load
Output Voltage Tolerance:#ERROR!
Output Connections:1) Hard Wire 5-wire (3PH + N + G)
Required Output Current Protection:250A
Neutral output current:400A
Bypass:Built-in Static Bypass
Input:
Nominal Input Voltage:400V 3PH
Input frequency:40 - 70 Hz
Input Connections:Hard Wire 5-wire (3PH + N + G)
Efficiency at Full Load:0.95
Input Total Harmonic Distortion:Less than 5% for full load
Battery Backup:15 Min at Full Load
|  | Carried to Summary |  |  |  | 0
| 5 | Power Cable
| 5.1 | From CMDB-1 to Xray
|  | 3x35+16mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 70 |  | 0
| 5.2 | From CMDB-1 to OPR
|  | 3x95+50mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 265 |  | 0
| 5.3 | From Transformer to ATS-1
|  | 240+120 mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 35 |  | 0
| 5.4 | From CMDB-1 to ATS-1
|  | 240+120 mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 15 |  | 0
| 5.5 | From Gen-1 to ATS-1
|  | 240+120 mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 35 |  | 0
| 5.6 | From MDB Xray to SDB LAB
|  | 4x6mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 55 |  | 0
| 5.7 | From MDB Xray to SDB ADMIN
|  | 4x4mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 55 |  | 0
| 5.8 | From MDB OPR to SDB OPR
|  | 4x6mmsq ,Cu/XLPE/PVC ,0.6/1KV | Meter | 55 |  | 0
|  | Carried to Summary |  |  |  | 0
| 6 | Grounding System
Complete grounding system for transformer, generator ,low voltage switch gear and all distribution boards as per IEC,EN or BS standards attain 5 ohms with complete inspection pits as per the detail drawings bare copper wire ,copper rods of appropriate size conducting materials and approved type of networks complete accessories. Note:- If the earth resistance is more than 5 ohms add additional electrode spaced at length of the electrode
| 6.1 | Earthing Rod, 16mm diam, 1500 mm bare copper wire | Pcs | 3 |  | 0
| 6.2 | Erathing Cable, Yellow/Green, 1x16mmsq | mt | 220 |  | 0
| 6.3 | Supply and lay PVC pipe of diameter 110mm , PN 6 for power lines from transformer & standby generator to MDB. MDB-to sub distribution boards. Price includes excavation & Earth work, sand beading ,any incidental civil works and backfill in order to install the cable and connecting manhole to manholes. | Meter | 600 |  | 0
Manhole
| 6.4 | Construct earthling manhole with brick wall 250mm thick on mass concrete bed of 100mm, with inside walls to be plastered in two coats of cement mortar, with reinforced concrete slab cover of 60mm thick ( C-25, reinforcement bars 8 diam , centre to centre 150 mm spacing) , steel bar handle and having internal dimensions of 60x60x60cms. Price alsh include excavationand earth work , back fill and cart away max 5 kilometer from site to complete the work | No | 6 |  | 0
|  | Carried to Summary |  |  |  | 0
| 7 | Generator
| 7.1 | Generator 1, Standby Power of 200 KVA (See attached spec) | PCs | 1 |  | 0
| 7.2 | Operation and Maintenance Training Program for Hospital technical team (see technical specs) | Ls | 1 |  | 0
|  | Carried to Summary |  |  |  | 0