UPDATED NEEDS ASSESSMENT FOR ADWA-ABA’ALA HOSPITALS REHABILITATION PROJECT

ADWA-ABALA HOSPITALS’ REHABILITATION PROJECT

August, 2025

Contents

1.	Executive Summary	2

2.	Introduction	2

3.	Objective	3

4.	General status of the hospitals	3

4.1.	Adwa General Hospital	3

4.2.	Abala’a Primary Hospital	4

5.	Identification of Rehabilitation Needs	5

5.1.	Component I: Adwa General Hospital Rehabilitation Plan	5

Findings and Proposed interventions	5

i.	Construction of segregation block	7

ii.	Construction of oven type incinerator	7

iii.	Supply and installation of prefabricated diesel incinerator	8

iv.	Ash pit construction	8

v.	Placenta pit	8

vi.	Glass crusher and compactor	8

vii.	Establishment of a One Stop Center	11

5.2.	Component II: Aba'ala Primary Hospital Rehabilitation Plan	13

5.2.1.	Rehabilitation of Electrical system	13

5.2.2.	Rehabilitation of damaged infrastructure works	14

5.2.3.	Solid waste zone rehabilitation and improvement work	14

Need for a New Service Block	15

i.	Emergency Block	15

ii.	Operation Theatre	15

5.2.4. Establishment of a One Stop Center 	15

5.2.5.	Medical equipment supply	18

6.	Conclusion	18

# Executive Summary

The northern Ethiopian conflict has impacted the healthcare infrastructures facilities across the affected regions, severely Afar and Tigray regions. Aba'ala Primary Hospital and Adawa General Hospital, two critical healthcare facilities in these regions, have been heavily damaged by armed conflict, resulting in loss of services, serious infrastructure, and medical equipment. This consolidated report provides a comprehensive plan for the rehabilitation and re-equipping of both hospitals to restore essential health services, enhance resilience, and meet the increasing healthcare needs of their respective catchment populations.

The primary objective of this consolidated intervention is to rehabilitate damaged infrastructure, re-establish reliable power and water supplies, restore diagnostic and treatment capabilities, improve waste management systems, upgraded and equipped One-Stop Centers (OSCs) for comprehensive Gender-Based Violence prevention and response in both hospitals. Specific interventions are designed to address each hospital's unique challenges while contributing to a unified goal of resilient healthcare service delivery.

# Introduction

The recent civil conflict in northern Ethiopia caused widespread destruction of healthcare facilities, worsening the already fragile healthcare system in regions such as Afar and Tigray. Aba'ala Primary Hospital in Afar and Adwa General Hospital in Tigray have both experienced severe damage due to looting, destruction of infrastructure, and equipment loss. Despite efforts to resume limited operations, both hospitals currently function well below capacity and cannot meet the healthcare demands of their communities.

This document presents a unified plan to rehabilitate and enhance these hospitals by outlining the existing conditions, identifying key rehabilitation areas and proposing specific interventions for secured budgets. The interventions target important areas such as water supply, electrical systems, infrastructure repair, medical equipment replacement, and solid and liquid waste management. Through this joint approach, the report aims to implement the required intervention through the secured fund to restore and enhance the operational capacities of these hospitals.

Objective

This consolidated updated report aims to:

- Present a comprehensive and executable rehabilitation and equipment restoration strategy for Aba'ala Primary Hospital and Adwa General Hospital.

- Ensure hospitals are equipped to deliver uninterrupted and quality healthcare services to their catchment populations.

- Restore essential healthcare services, and utilities disrupted by conflict.

- Improve hospital resilience and readiness for future emergencies through sustainable systems, including solar energy and advanced waste management.

- Establish inclusive One-Stop Centres to enhance protection, safety, and support for GBV survivors through gender-sensitive and coordinated responses.

# General status of the hospitals

# Adwa General Hospital

The hospital is multi-specialty a secondary (general) hospital in the health care system of the country. The hospital was extending its service 110 in-patient bed services, 8 pre and 14 post labour beds, 15 emergency beds, 4 operation theatres table with 8 recovery beds with each monitor and 20 beds for neonatal intensive care unit. Currently only 50 beds are available and the remaining are either looted or damaged.  In general, the hospital gives four major specialties as an outpatient and inpatient service these are paediatrics, surgery, internal medicine, maternity and other specialty services.

In terms of diagnostic laboratory and imaging the hospital owned sophisticated laboratory machines, digital X-ray, ultrasound and endoscopic services. The hospital was damaged twice by the armed groups in 2020 and 2022. During the conflict almost all of the major and minor medical equipment, non-medical items and different kinds of medicines (drugs) of the hospital were looted and damaged by armed groups. The hospital ceased its services for six months after the second round damage.

The hospital comprises two distinct segments in terms of its building infrastructure.

- Old Buildings:

- The existing structures, established during the reign of Emperor Haile Selassie in 1936, were originally designed to serve to a population of approximately 5,000. Embracing nine blocks, all these buildings are single-story structures.

- The new expansion, (SB+G+2) hospital building which was interrupted by the conflict intentioned to accommodate 420 inpatient beds and will offer various hospital services within a modern hospital infrastructure. Before the onset of the recent conflict, the hospital played a vital role in providing to a population of approximately 1.2 million across eleven (11) administrative Woredas. Additionally, it functioned as a referral hospital for three primary hospitals, 35 health centres, and 100 health posts. The hospital's catchment area, characterized by dense population, also accommodated hundreds of thousands of IDPs residing in the town.

The status of this expansion of hospital with construction of new building at current stage shows that the primary structure of the building, including partition walls, flooring works, electric wiring and plastering work has been completed for the basement, ground, first, and second floors.

Currently, the hospital is operating under its capacity due to the damages without having major medical equipment like imaging and laboratory equipment. The overall infrastructure rehabilitation\ improvement areas and equipment needs are identified and presented as follows.

# Abala’a Primary Hospital

Aba’ala primary Hospital is found in the Northern part of Ethiopia in Afar Region which is Nine hundred ninety eight (998) kilometre from Addis Ababa and fifty kilometres, (50kms) from Tigray regional capital Mekelle.  Aba’ala has an estimated total population of sixty thousand six hundred by the year of 2023. The hospital provides medical care to the surrounding area, which has an estimated catchment population of eighty thousand (8,000).

The Afar region is one of the most affected zone among the northern part of Ethiopia due to the recent conflict, and huge destruction of health infrastructures, medical and non-medical equipment damage and looting were recorded.

This zone has two (2) hospitals, twenty one (21) health centres, one hundred five health posts (105) and five (5) private clinics.

During the invasion of the region, most of the health institutions have been affected in many ways; it targeted and destroyed hospitals, health centres, and health posts, as well as the supplies, drugs, Medical equipment, public infrastructures and other essential commodities they were providing to the population. Among the health facilities on the region of Afar Aba’ala hospital need special support in infrastructure rehabilitation and re-equipping.

Currently, Aba’ala Primary Hospital is giving services to the community at a capacity below its potential, lacking almost all medical equipment such as imaging and laboratory facilities, no water supply system, extreme power shortage, fluctuation and total electric system damage. Additionally, the infrastructures are damaged, impacting the hospital's ability to deliver services effectively. These challenges demand urgent attention and intervention.

# Identification of Rehabilitation Needs

## Component I: Adwa General Hospital Rehabilitation Plan

In the premises of Adwa Hospital, number service buildings are present, including a new building intended as an expansion of the existing hospital blocks.

Due to the conflict, electrical system, water supply, door and windows of the old buildings and construction materials for the new expansion project, were damaged and looted by the armed groups, and the hospital was out of service for 6 months.

The SB+G+2 (semi basement plus ground plus two) building which is an expansion project for the hospital were in active construction stage before the conflict and suppose to complete on 2020. However, due to the conflict all onsite construction materials were looted and the construction works of the new building is terminated. The existing buildings are old and cannot satisfy the needs of the hospital since they are designed long ago for small number of population.

## Findings and Proposed interventions

    - Renovation, restoration, rebuilding

During our assessment, it has been practically observed that renovating the old building is not a feasible option because various reasons. From the very beginning, MoH in collaboration with Tigray region health bureau invested on the construction of new building due to the increase in the number of beneficiaries of the hospital and less feasibilities to renovate the old and depreciated blocks.  Instead, Expertise France, in collaboration with the hospital management team and the regional health bureau, strongly suggested that renovating fully or partly of the newly constructed expansion building depending on the availability of the budget. This recommendation aims to transfer some crucial services that are currently congested and non-functional in the old building. Number of reasons that supports this recommendation, as outlined below:

- Structural Integrity:

The current service spaces within the existing old buildings are insufficient to accommodate both the planned medical equipment and the anticipated required space. This inadequacy is making worse by the on-going service expansion, directly correlated with the increasing population.

Furthermore, the structural integrity of the old buildings has been compromised over time due to wear and tear. This condition poses significant challenges, as restoring them to modern safety standards would be both intricate and costly. In light of these limitations, considering the construction of a new facility becomes a more practical and sustainable solution to meet the growing needs of the healthcare institution.

- Space Optimization and technology upgrades :

The new building is planned and optimized for space utilization, in order to provide better layouts for medical services, patient flow, and administrative functions compared to existing structures. Expertise France assessed the new building and proposed to focus to restore on one wing, mainly it is designed to meet current building codes, safety regulations, and healthcare standards, ensuring full compliance with contemporary requirements. This new building allows for flexibility and adaptability to future changes in healthcare requirements and technologies.

- Functionality Requirements: The growing needs of a healthcare facility, such as the demand for specialized medical equipment and expanded services, may not align with the layout and design limitations of old buildings.

- Cost-effectiveness:

In this case, the cost of renovating the old buildings, including addressing unforeseen issues, will exceed the cost of constructing / finalizing one wing as essential part of the new building.

- Long-term Sustainability:

The new building EF propose to finalize corporates justifiable design practices and materials that contribute to long-term environmental and operational sustainability. It also enhances the overall image of the healthcare institution, instilling confidence in patients, staff, and the community.

The interventions proposed under the new building blocks are:-

- Furnishing the new building block floor finish and wall finishing

- Fixing window door

- Roofing, Ceiling works, Painting works and other building finishing works

- Supply and install internal pipe lines

- Supplying and installing sanitary fixtures according to specified standards, including those required for operating rooms and toilets, while also ensuring accessibility for individuals with special needs.

- Access road from the main entrance to the new building

    - Solid Waste management

It appears that critical elements of efficient medical solid waste management, including as segregation, collection, storage, transportation, treatment, and disposal, are rarely put into practice at Adwa General Hospital.

The hospital previously had an oven-type incinerator that has now completely collapsed. Additionally, there is an inadequate disposal area for placenta, and the designated pit for placenta disposal has also collapsed.

The on-site incinerator is entirely ineffective, and waste is burned outdoors in an open chamber without proper solid waste segregation. This unsafe method causes risks for employees and has the potential to contaminate and disperse potentially hazardous airborne particles, affecting not only individuals with respiratory issues but all forms of life.

The interventions proposed under solid waste management are:-

To solve the existing problems regarding lack of improved solid waste management facilities in the hospital, the project come up with the following designs to reduce the spreading of the infectious germs and others.

The intervention design suggested that the solid waste zone to be separate zone and be accessed by designated departments of the hospital.

## Construction of segregation block

The hospital generates two type solid wastes, hazardous and non-hazardous wastes. To dispose those wastes the first step is to segregation wastes. Therefore, it is proposed segregation block with five sections to separate the coming wastes from different departments of the hospital blocks. This block also facilitates segregated storage to practice recycling of materials such as plastic, metal, and other recyclables within the hospital. This initiative aims to reduce the environmental impact of burning such materials.

## Construction of oven type incinerator

The intervention proposed independent block which is constructed by fire rated brick in order to burn non-hazardous wastes.

## Supply and installation of prefabricated diesel incinerator

Thee intervention proposed to supply and install power driven incinerator in order to burn hazardous wastes.

## Ash pit construction

The proposed intervention indicates construction of ash pits is to dispose the ash from medical hazardous waste of incineration.

## Placenta pit

This is necessary part of the hospital at MCH building block and it is proposed to be constructed a concrete pit in separate area which is design to hold and process for the future expansion of the project in the hospital premises.

## Glass crusher and compactor

This section is designated for crushing glass from medical and non-medical sources to facilitate recycling and minimize the space occupied by waste. Additionally, a compactor is included to compress plastic and cardboard waste generated by the hospital. The design proposal incorporates a simple hydraulic system for easy operation by the cleaning staff.

    - Liquid Waste Management

The hospital is embraced of a wide range of services and functional units. These include diagnostic and treatment function, such as clinical laboratory, imaging, emergency rooms, and surgery; and hospitality functions, such as food service and housekeeping and the fundamental inpatient care or bed-related function.

During the assessment we have observed that most of the hospital’s liquid waste lines, particularly those at diagnostic centres, MCH, laundry and kitchen blocks are broken and do not drain the waste to safe place. Mainly the hospital’s site liquid waste lines and its connections have been broken. Sewer manhole intervals are wider than required, making inspection difficult. In the hospital compound, there are roughly five septic tanks, but for various reasons, most of them have failed and the liquid waste is now connected to nearby river.

Interventions of efficient liquid waste management at this hospitals is crucial in order to prevent the spread of infections, protect the environment and safeguard public health by properly treating and disposing of potentially hazardous liquids generated during medical services to the patients.

The interventions proposed under liquid waste management are-

To address the environmental impact caused by the collapsed liquid waste management system at the hospital, an intervention for infection prevention and environmental remediation is necessary. This includes

- The implementation of a new design for the sanitary network (the old facility and new one) and liquid waste treatment.

- Construction of primary liquid waste treatment :

- Dilution Pits: - In this stage the proposal considered construction of dilution pits immediately from laboratory blocks, OR blocks to dilution the chemicals before reaching to the next storage tanker.

- Grease/ Oil separator:- Hospitals often generate wastewater that contains fats, oils, and grease (FOG) from kitchen or medical processes. Grease traps or oil-water separators can be employed to remove these substances before they can cause issues in downstream treatment processes or the sewer system. Oil separator pit construction in this part near to the kitchen block oily wastes will be treated before reaching to the next storage tanker.

- Secondary stage waste treatment: - In this stage the intervention considers construction equalization tank. The construction of a septic tank typically involves several chambers or compartments that facilitate the treatment and separation of solids from wastewater.

- Tertiary stage planting a waste treatment plant

- Waste water Technology System:-The proposed waste water treatment is the most sustainable, eco-friendly and cost-effective wastewater treatment solutions for hospitals. With its small footprint and scalability, it can be installed wherever wastewater is generated, regardless of size and capacity. The proposed waste water treatment is High-Speed MBBR – STP which will treat the waste water and to be discharged to the nearby river with irrigation water standard or to re-used for cleaning and laundry purposed.

    - Electrical, electro mechanical and power backups

Before the conflict, the hospital had access to two power sources: the national electric grid and three standby generators with capacities of 205, 160, and 100 (KVA) respectively. Unfortunately, all of the generators were damaged, leaving the hospital reliant solely on grid power, which itself is subject to fluctuations as a result of the conflict.

During the assessment, it was noted that the electrical installation for the new hospital block had been partially completed by the previous contractor. However, essential components such as the main distribution board and other electrical sub-distribution boards were not installed, and electrical fixtures remained unfixed.

As a critical facility, the hospital is expected to maintain uninterrupted power availability to support vital services, particularly within operation theatres and critical rooms where continuous electricity is critical for the proper operation of medical equipment and life-saving procedures. However, the hospital currently lacks a reliable backup power source in case of interruptions from the normal grid line. Thus, an intervention to supply and install additional generators and solar panels is significant for the hospital due to its reliance on major electric power supply, which is vulnerable to disruptions, particularly during emergencies. Therefore, enhancing the hospital's power backup infrastructure through the installation of generators and solar panels is essential to mitigate the risks posed by power outages and ensure seamless operations, ultimately safeguarding the well-being of patients and the effectiveness of medical care delivery.

Therefore, it is imperative to intervene and complete the finalization process in the designated section of the hospital where our intervention is proposed.

The interventions proposed under Electrical and electro-mechanical installation work are:-

- Assisting the hospital in upgrading the transformer capacity by assessing the demand and future expansion requirements.

- As per the design and specification of the new building providing and installing internal electrical and electromechanical systems.

- Fixing corresponding electrical distribution boards

- Supply and fixing electrical fixtures

- Introduce, supply and install alternative source of power and power backups

- Solar system

- Backup battery

- Equivalent capacity Generator with the transformer

    - Equipment and Machineries

During the conflict the hospital’s major medical and non-medical equipment and record systems have been damages and looted.

To ensure the hospital functions at its maximum capacity and accommodates both current needs and future expansions, it requires essential medical and non-medical equipment. This intervention is vital for providing adequate healthcare services to the local community.

The need assessment has been conducted twice to accurately identify the hospital's necessities, with collaboration between the regional health bureau and the hospital management team.

### Establishment of One Stop Center

Establishing a One Stop Center for Comprehensive GBV Prevention and Response in post conflict areas is crucial for addressing survivors' complex needs, promoting healing, and strengthening community resilience. In the aftermath of recent conflict, the affected community has experienced a significant rise in GBV cases and trauma over the past three years. Although underreporting due to stigma complicates data collection, community reports confirm that GBV remains a pressing and persistent issue.

According to data from Adwa City’s Women, Children, and Social Affairs Bureau, the city has approximately 197,634 residents, including over 105,000 displaced persons in six IDP camps. In 2017 E.C., over 2,135 GBV cases were registered, involving children and survivors with children, often with unknown perpetrators. Many survivors lack access to timely services due to resource shortages and logistical barriers, resulting in outcomes such as 86 HIV-positive cases, 101 unsafe abortions, 55 disabilities from physical violence, 43 mental health issues, 32 children with unknown fathers or perpetrators, 140 STIs, 36 cases of sexual violence involving children, and five deaths.

In response, Adwa Hospital has repurposed its staff residence as a GBV prevention and response clinic. However, despite the high number of cases, only 632 survivors received first-line medical support at Adwa hospital in 2017 E.C.

The current GBV prevention and response clinic of Adwa hospital has several limitations:

- It provides only basic medical support and does not function as a full-fledged One-Stop Center.

- It is understaffed, poorly equipped, and lacks the necessary infrastructure, resources, and a survivor-centered environment to ensure safe, confidential, and comprehensive care.

- Healthcare workers require additional training in survivor-centered approaches, mental health and psycho-social support, and effective referral systems.

- Many community members are unaware of the available GBV response services at the hospital.

- Economic challenges prevent many survivors from covering transportation costs to access a comprehensive specialised services at other service centers.

- Coordination among protection actors in Adwa town is weak, and referral systems are underdeveloped.

These issues significantly limit the overall effectiveness of GBV response efforts in Adwa town. As a result, services remain limited and poorly integrated, leaving survivors without holistic support that encompasses medical treatment, psychological counselling, legal aid, and social reintegration.

Given the scale and sensitivity of GBV needs, immediate intervention is crucial. Establishing a dedicated, fully equipped One-Stop Center within Adwa Hospital will ensure:

- Adequate infrastructure, staffing, and supplies

- Private, trauma-informed environments for survivors

- Integrated services, including medical, psychological, and legal support

- Enhanced capacity for dignified and professional response

- Stronger referral linkages and coordination among service providers

This center will greatly improve the quality and accessibility of care for GBV survivors, promoting healing and resilience within the community.

Fig. 1. The Current Status of GBV Response Service Centers at Adwa Hospital

## Component II: Aba'ala Primary Hospital Rehabilitation Plan

Our team has conducted multiple visits to Afar, specifically Aba'ala, to conduct a comprehensive and detailed assessment of the Aba'ala Primary Hospital. During our assessment we have seen in detail the hospital basic rehabilitation needs the infrastructure vandalism, electrical systems damage and power shortage, critical water supply problem, insufficient medical equipment and additional need of mandatory infrastructures. Each need is carefully analysed, emphasizing the impact on patient care and the urgent requirement for rehabilitation

### Rehabilitation of Electrical system

According to our assessment before the conflict the hospital had sufficient electric power sources, including its own transformer from the ELPA grid line and a standby generator (110KVA). Unfortunately, during the conflict, extensive damage occurred to the hospital's transformer, standby generator, main distribution boards, sub-distribution boards, and electric line installations, resulting in a significant electrical power problem.

Following the conflict, the hospital has been facing persistent power shortages, forcing staff to schedule the use of medical equipment rather than operate them simultaneously. This significantly limits service efficiency and response time. Additionally, the hospital's electrical system requires urgent enhancement to support the safe and reliable operation of critical equipment. With rapid population growth and increasing demand for healthcare services, upgrading both the hospital’s infrastructure and electrical system is essential. Despite being the main healthcare provider in the area, the hospital is currently unable to operate at its full potential.

To address this critical problem, our team proposes the installation of upgraded electrical systems. Due to frequent power fluctuations, the hospital urgently requires reliable backup systems to support critical healthcare services. In response, our team has proposed the integration of an additional alternative power source using a solar energy system. This solution is expected to significantly enhance the reliability and stability of the hospital’s electrical infrastructure, while also reducing the risks associated with on-going power outages. By implementing this alternative energy system, we aim to fully restore the hospital’s operational capacity and ensure the continuous delivery of essential healthcare services to the community.

### Rehabilitation of damaged infrastructure works

The hospital was once captured by the armed groups and damaged some parts of infrastructures, most significantly building block's window-doors breaking, glazing smashing, roof and other facility destructions.

To improve this damaged infrastructure and make the hospital functional and perform in its full potential our team analysed and identified the Re-furnish damaged infrastructures and improvement works. The detail quantity for this work is attached to this document.

### Solid waste zone rehabilitation and improvement work

The hospital has a good system for segregating garbage but a bad arrangement for disposing of it; all wastes from wards, offices, and other spaces are collected in a well-organized bin and placed in the waste disposal zone. However, the quantity of bins is insufficient to provide the service to its maximum potential, the existing incinerator (traditional oven type incinerator) is not functioning at all, all hospital solid waste is burned in an ordinary chamber, which is hazardous and takes a long time, especially when burning waste from the safe box.

Since the compound has enough space for the renovation and expansion of the different solid waste management facilities. Our team believe expansion of solid waste zone within the hospital will solve the hospitals sanitation problem. This includes the construction of appropriate waste disposal systems, such as power driven incinerators, segregation zone, recycling facilities, as well as the implementation of efficient waste management protocols.

## Need for a New Service Block

### Emergency Block

The current emergency department has been allocated a small room originally designated from one of outpatient services rooms. This space is significantly inadequate in both size and function to support even the current demand of emergency cases. The infrastructure is below standard, lacking the essential layout, patient flow design, and life-saving equipment typically required in a modern emergency care setting.

Given the increasing demand for emergency services, there is an urgent need to construct a dedicated, fully equipped emergency service block that ensures safe, efficient, and dignified care for patients.

### Operation Theatre

The existing operation theatre is critically underdeveloped, both in structure and in the space required to accommodate modern surgical procedures. The facility is lacking the necessary areas for pre-operative preparation, sterile zones, anaesthesia induction, recovery rooms, and support spaces. This challenges both patient safety and surgical efficiency.

Furthermore, the inadequate infrastructure restricts the number and types of surgical cases that can be performed, causes procedural delays, and increases the risk of infection and post-operative complications. With rising surgical demands and the hospital’s role as a primary referral center, a new, purpose-built operation theatre block is essential. This block should be equipped to handle emergency and elective surgeries, meet infection control standards, and provide appropriate working conditions for surgical teams.

### Construction of a One Stop Center at Abala Hospital

Establishing a dedicated Gender-Based Violence prevention and response centre in post conflict areas is crucial for addressing survivors' complex needs, promoting healing, and strengthening community resilience.

The Abala Hospital One Stop Center was rapidly established in response to the northern Ethiopia crisis, aiming to provide essential GBV response services in a conflict-affected, underserved area. Currently, the OSC operates within a building originally constructed for laundry and cafeteria purposes, which makes it structurally unsuitable for survivor centered services. The facility lacks dedicated rooms such as legal support offices, counselling spaces, child-friendly areas, and private treatment rooms. As a result, the environment is neither confidential nor secure, compromising survivor dignity and safety.

Despite efforts by various donors to furnish the center, most materials furniture, computers, tables, chairs, and other equipment are repurposed for other departments in the hospital and are not functional within the OSC. This limits service delivery, forcing staff to operate on an ad hoc basis or only when cases are reported. Moreover, there are no designated spaces for police, prosecutors, or legal officers, and their absence affects the quality and timeliness of legal assistance. While police and legal personnel are deployed, they lack proper furniture, rooms, or training on survivor cantered approaches, further hampering effective response.

Staffing levels are critically low. The OSC functions with only five staff members comprising a OSC coordinator, a nurse, a social worker, and two support staff well below the standard requirement of at least eleven trained professionals. This shortage leads to overburdened staff, inconsistent service provision, and limited capacity to deliver comprehensive care, including mental health support. The hospital lacks dedicated psychiatrists and psychologists; survivors needing such services are referred to distant facilities like Mekele or Dubti, with transportation costs posing additional barriers.

Medical supplies for GBV survivors are insufficient. While HIV medications are donated and provided free of charge, other essential medications such as STI prophylactics, emergency contraceptives, and psychosocial medicines are not consistently supplied, leading to gaps in free, comprehensive treatment. The hospital cannot fully guarantee free services due to resource shortages, staffing gaps, and financial constraints. This situation discourages survivors from seeking care and affects the quality of the response.

Coordination among protection actors is weak. Many NGOs operate independently, often targeting the same communities and activities without proper planning or resource sharing, resulting in duplication and inefficient use of limited resources. Community awareness about available services remains low; cultural taboos and lack of outreach hinder utilization, especially since GBV response service utilization is often stigmatized or considered taboo.

Major challenges include:

- Infrastructural deficiencies and lack of a purpose-built, confidential, and survivor-friendly facility.

- Inadequate staffing, high turnover, and lack of specialized mental health professionals.

- Insufficient furnishings and medical supplies, hampering service quality.

- Lack of trained personnel, especially police and prosecutors, on survivor-centered procedures.

- Limited resources for free treatment, with some essential supplies not donated or funded.

- Poor coordination and overlapping efforts among NGOs, leading to resource duplication and gaps in service coverage.

Recommendations include:

- Constructing a standardized, fully equipped, and survivor-friendly OSC with dedicated spaces for legal, medical, and psychosocial services.

- Equipping the center with furniture, medical supplies, and communication tools.

- Building staff capacity through comprehensive training on survivor-centered, trauma-informed care, and legal procedures; recruiting more qualified staff, including psychologists and legal officers.

- Securing donor or government support to provide free medications and supplies, removing financial barriers.

- Strengthening coordination among protection actors through formal MoUs, joint planning, and shared monitoring systems to prevent duplication and improve resource efficiency.

- Conducting community awareness campaigns to increase service utilization and change attitudes towards seeking help for GBV.

- Making the functionality of the OSC a performance criterion for hospitals to ensure sustained attention and resource allocation from authorities.

- Engaging regional and national authorities to address staffing shortages and resource gaps, especially for free medication supplies.

During this assessment EF try to motive the concerned stakeholders to be responsible for the functionality of Abala hospital OSC. As the result, hospital and protection sector leaders have expressed strong willingness to improve the OSC. The hospital has facilitated a dedicated room for police and prosecutors, and personnel have been deployed to work regularly within the center. These commitments form a foundation to develop a fully functional, effective GBV response facility that respects survivor dignity, promotes access, and enhances coordination among all actors involved.

Fig. 2. The current status of Abala Hospital One stop center

### Medical equipment supply

The hospital re-opened after the conflict by partly rehabilitating it, although it is not fully operational due to the looting of laboratory, diagnostic, and other hospital medical equipment. The hospital requires replacement of looted equipment as well as additional machinery to meet the institution's overall requirement.

To determine the exact requirements for essential medical equipment, we propose conducting a comprehensive needs assessment. This assessment help to identify the specific equipment needed for accurate diagnoses, effective treatments, and improved patient outcomes.

# Conclusion

The conflict in northern Ethiopia has had devastating impacts on the region, resulting in the widespread destruction of infrastructure and disruption of essential public services. Aba’ala Primary Hospital and Adwa General Hospital both vital healthcare institutions serving their respective communities have not been spared. They have faced significant structural damage and numerous operational challenges that have hindered their ability to deliver quality healthcare services, particularly to vulnerable populations including women, children, and conflict survivors.

This assessment has updated rehabilitation needs common to both hospitals, including the establishment of a sustainable water supply, rehabilitation of electrical systems, repair of damaged infrastructure, improvement of solid and liquid waste management systems, and the acquisition of essential medical equipment. In addition, the establishment of a One stop center at both hospitals is a major milestone, enabling the hospitals to provide dedicated and comprehensive support services for survivors of violence. At Adwa General Hospital, a key intervention includes the installation of a liquid waste management system to improve sanitation, protect the environment, and support safe healthcare operations.