## Datasheet
Modèle de l'équipement :
Liste des Equipements & sous-equipements
Nom | Location (Fab or sub-fab) | Type (Chiller, pump…) | Model | Dimensions (L x w x h) in mm |  | Weight (Kg) |  | Supplied by
Chiller = Régulateur Thermique 1 | Sub-Fab | Heat Exchanger | NESLAB HX-150 | 500 x 600 x 900 |  | 400 |  | Supplier | EXEMPLE
Pump 1 | Sub-Fab | Pump | iHx 600 | 300 x 900 x 800 |  | 200 |  | LITEN | EXEMPLE
Mainframe | Fab | Mainframe | xxx | 2500 x 1300 x 2600 |  | 2500 |  | Supplier | EXEMPLE
Dimensionnement nécessaire des facilities pour le bon fonctionnement de l'équipement |  |  |  | Connection |  | Consumption (e) = "Consomation" |  |  |  | Pressure (bar) at the connection on the tool |  | Temp (° C) |  | Purity
Fluid (a) | From | To | Description (b) | ID (c.) | Size (d) | Type | Min | Max | Average | Min | Max | Min | Max |  | Supplied by | Comments (ex: max length..) (f)
N2S | Facilities | Mainframe CH A | N2 Purge | G1 | 1/4" | VCRM | 15 | 50 | 25 | 2.5 | 5 | N/A | N/A | N/A | LITEN | Exemple
Glycol | Chiller 1 | Mainframe CH A | Chilled Water | F1 | 3/8" | swg | 10 | 20 | 12 | 2 | 3 | 15 | 18 | N/A | Supplier | installed by LITEN Exemple
BCl3 | Facilities | Mainframe CH A | BCl3 proces | J2 | 1/4" | VCRM | 1 | 2 | 1.2 | 1 | 1.3 | N/A | N/A | N50 | LITEN | Purity : N50
Comments
(a): Voir feuille "Fluids" pour quelques exemples
(b): Pour décrire le but et les caractéréistiques de connexion
(c): Nom de la connexion identifiée sur l'équipement
(d): Taille de la connexion, l'unité doit être précisée
(e): Flows (débit entrant et sortant) et consommations qui doivent être converti comme décrit ci-dessous :
Exhaust : m3/h
ERP (PCW), EDI (DIW), VP, drain : l/min
Gaz : Slm (Standard liter per minute)
(f): Mettre les remarques et contraintes à connaître pour l'installation de l'équipement : par exemple longueur maximale, …
Exigences Electriques
From | To | Type (power, signal..) | Voltage | Phases | Breaker Amp = limite en ampères de sécurité | FLA (Full Load Amperage) | Average Amp | Supplied by | Installed by
Power Box | Mainframe | Power | 400 | 3 | 100 | 75 | 35 | LITEN | LITEN | Exemple
Mainframe | Pump | Power | 400 | 3 | 80 | 60 | 30 | Suppplier | LITEN | Exemple
Mainframe | Chiller | Signal | 24 | 1 | NA | NA | NA | Supplier | Supplier | Exemple
Nuisances
From | To | Type (power, signal..) | Voltage | Phases | Breaker Amp = limite en ampères de sécurité | FLA (Full Load Amperage) | Average Amp | Supplied by | Installed by
Power Box | Mainframe | Power | 400 | 3 | 100 | 75 | 35 | LITEN | LITEN | Exemple
Mainframe | Pump | Power | 400 | 3 | 80 | 60 | 30 | Suppplier | LITEN
Mainframe | Chiller | Signal | 24 | 1 | NA | NA | NA | Supplier | Supplier
Nuisances |  | unité | niveau
Descriptif sécurité à joindre | Bruit | dB
Vibrations
Rayon x
Magnétique
Poussières
Particules "nano"
ANNEXE 2 : Spécifications pour l'installation d'un équipement
1) Cette annexe permettra au CEA de réaliser le PID pour les fluides et PID électrique.
2) Ces PIDs seront alors envoyés pour vérification au fournisseur de l'équipement pour approbation.
3) Le Hook Up et le Fit Up débuteront après la validation officielle des PID par le fournisseur.

## Fluids
Fluids | Descriptions
ACS / CDA | Air Comprimé Sec / Compressed Dry Air
N2S | Nitrogen Service
N2P | Nitrogen Process
Ar | Argon Process
He | Helium Process
Exhaust | Exhaust
Acid Drain | Acid Drain
HF Drain | HF Drain (if [HF] > 1%)
Solvent Drain | Solvent Drain
ERP / PCW | Eau de Refroidissement Process / Process Cooling Water
EDI / DIW | Eau Dé-Ionisée / Deionised Water
VP | Vide Process / Vacuum (P=-880mbar) (expect pump)
Process Gas | Example : H2, SiH4, CH4…
Process Fluid | Example : IPA, HF, H3PO4…