# Methodology for baseline energy consumption
MESCO ToolBox

TABLE OF CONTENTS

1.	Introduction	3

2.	Normative references	3

3.	Methodology	4

3.1.	Baseline energy consumption	4

3.1.1	Calculation of the baseline thermal energy consumption	4

3.1.2.	Calculation of the baseline electrical energy consumption	10

3.2.	Verification	11

3.2.1.	Verification of thermal energy consumption (post Implementation)	11

3.2.2.	Verification of electrical energy consumption	12

3.2.3.	Verification of overall energy savings	13

3.3.	Methodology limitations and adjustment protoCols	13

3.3.1.	Criteria for recalculations	13

3.3.2.	Expansion or reduction of the building's heated area or occupancy	14

3.3.3.	Complete repurposing of building usage	14

# Introduction

This document outlines a comprehensive methodology designed to calculate the baseline energy consumption in buildings. It encompasses detailed procedures for verifying various aspects of energy savings, including:

- Thermal Energy Savings

  - heating energy savings

  - DHW energy savings

  - ventilation energy savings

- Electrical Energy Savings

Additionally, this document includes practical examples of calculations using a specially developed MS Excel tool, tailored for this purpose. To ensure clarity and precision in application, the document also delineates the limitations of the methodology. This is intended to provide clear guidance for scenarios that may not be directly covered by the calculations outlined in this methodology.

# Normative references

This methodology incorporates references to several key normative documents that are integral to its framework:

- International Performance Measurement and Verification Protocol (IPMVP®): This protocol sets the standard for quantifying the performance of energy and water efficiency projects.

- ISO 50006 Energy Management Systems — Evaluating Energy Performance Using Energy Performance Indicators and Energy Baselines: This standard provides guidelines for establishing, using, and maintaining energy performance indicators and baselines as part of energy management systems.

- ISO 50015 Energy Management Systems — Measurement and Verification of Energy Performance of Organizations — General Principles and Guidance: This document offers comprehensive principles and guidance for measuring and verifying the energy performance of organizations within the context of an energy management system.

- SM EN 15378-3 Energy performance of buildings - Heating and DHW systems in buildings - Part 3: Measured energy performance, Module M3-10, M8-10.

- Law no 139/2018 (amended on 05.10.2023): This law implements the EU Directive 2012/27/EU in Moldova. It creates the legal framework for regulation of energy efficiency.

# Methodology

## Baseline energy consumption

The subsequent sections detail the methodology employed for the calculation of baseline energy consumption. This includes a comprehensive approach to accurately assess and verify thermal and electrical energy usage within buildings, encompassing various aspects such as heating, DHW, ventilation, and electrical systems. The methodology is designed to ensure precise and reliable calculations, adhering to the standards and principles outlined in the referenced normative documents. To consider the peculiarities of energy metering and measurement of influencing factors at the facilities, some calculations were refined.

### 3.1.1	Calculation of the baseline thermal energy consumption

The baseline thermal energy consumption for a period is determined using the following formula:

QB,i=QH,i+QDHW,i+QVe,i,  Gcal/period

Where:

QB	represents the baseline thermal energy consumption of the building, measured in Gcal/period.

i	denotes the specific period (usually – a month) for which the baseline thermal energy consumption is being calculated.

QH	is the baseline thermal energy consumption required for heating, expressed in Gcal/period.

QDHW	indicates the baseline thermal energy consumption necessary for domestic hot water (DHW) supply, also in Gcal/period.

QVe,i	is the baseline thermal energy consumption required for ventilation, measured in Gcal/period for the respective period.

The calculation of the baseline thermal energy consumption is based on the following data:

- Historical data on the actual consumption of thermal energy over the previous three years

- Heat supply agreement

- Information on the actual CO2 concentration during the operational period

- Information and data regarding the actual indoor temperature during the operational period.

#### Calculation of the baseline thermal energy consumption for DHW

In the absence of a separate metering unit for thermal energy dedicated to DHW supply and the availability of information related to charges for consumed heat energy for DHW supply, the monthly baseline thermal energy consumption for DHW supply throughout the year is calculated by analyzing DHW consumption during the summer period. This period is selected because it excludes thermal energy supplied for heating and ventilation purposes, providing a clearer indication of DHW consumption.

The process involves extracting DHW consumption data for the summer months. The consumption figures for each month are then divided by the number of working days in that month to determine the daily DHW consumption. These daily consumption figures are averaged to derive an average daily consumption rate for DHW preparation, applicable for the entire year. However, any consumption figures that fall below 80% or exceed 200% of this average are excluded from the calculation to account for potential anomalies due to system repairs or extraordinary circumstances.

##### Baseline Consumption (DHW) without separate meter

QDHW=K1mpni=1nQimetmiwp,  Gcal/period

Where:

QDHW	is the baseline thermal energy consumption required for DHW supply, expressed in Gcal/period.

K1	is a correction coefficient reflecting the period (heating or non heating) which considers the increase of thermal energy requirements for DHW supply during the heating period; specifically (K1 = 1.25) for the heating period and (K1= 1) for the non-heating period, calculated based on average temperature of cold water in the heating season (50C) and non-heating season (150C).

mp	represents the number of working days in the period for which the baseline thermal energy consumption is calculated.

n	is the number of periods (usually – months) over which the average consumption of thermal energy required for DHW supply has been calculated.

Qimet	denotes the consumption of thermal energy according to charges for period i, in Gcal/period.

miwp	is the number of working days during month i when DHW was supplied, excluding general educational institutions’ break periods.

The specific baseline consumption for DHW, measured in Gcal/working day, is refined using the following formula:

qDHW=1ni=1nQimetmiwp,  Gcal/working day

This formula is applied when there is no separate water heat meter installed specifically for DHW.

##### Baseline Consumption (DHW) with separate heat meter

The calculation is performed using the following expression:

QDHW=K1mpni=1nQimetK1imiwp,  Gcal/period

Where:

QDHW	is the baseline thermal energy consumption required for DHW supply, measures in Gcal/period.

K1	is a coefficient that corrects for the increase of thermal energy requirements for DHW supply during the heating period (K1 = 1.25) and non-heating period (K1= 1), calculated based on average temperature of cold water in the heating season (50C) and non-heating season (150C).

K1i	is a coefficient that corrects for the increase of thermal energy requirements for DHW supply during the heating period (K1 = 1.25) and non-heating period (K1= 1) in i period.

mp	represents the number of working days in the period for which the baseline thermal energy consumption is calculated.

n	is the number of periods (usually – months) over which the average consumption of thermal energy required for DHW supply has been calculated.

Qimet	denotes the consumption of thermal energy according to charges for period i, in Gcal/period.

miwp	is the number of working days during month i when DHW was supplied, excluding general educational institutions’ break periods.

In cases where data on daily or weekly thermal energy consumption during the non-heating period is available, the methodology for calculating the baseline thermal energy consumption required for DHW supply across all months (measured in Gcal/month) is refined as follows:

QDHW=K1mpni=1nQimetmiwp,  Gcal/period

Where:

QDHW	is the baseline thermal energy consumption required for DHW supply, Gcal/period.

Qimet	represents the consumption required for the DHW supply over the period i, Gcal.

miwp	is the number of working days during the period i, when DHW has been supplied (working days do not include the general educational institutions’ break periods).

This approach utilizes the available daily or weekly consumption data to provide a more accurate and representative baseline for DHW energy needs throughout the year.

To enhance accuracy and applicability under different scenarios, the methodology is updated with the specific baseline thermal energy consumption for DHW.

The specific baseline consumption for DHW, measured in Gcal/working day, is refined using the following formula:

qDHW=1ni=1nQimetmiwp,  Gcal/working day

This formula is applied when there is a separate heat meter installed specifically for DHW.

##### Baseline Consumption (DHW) with separate water meter

If a separate water meter for DHW (measured in cubic meters) has been installed at least 30 working days before the EPC procurement procedure, the baseline for DHW is refined as follows:

QDHW=0,04 K1mpni=1nGimetmiwp,  Gcal/period

Where:

QDHW	is the baseline thermal energy consumption required for DHW supply, measures in Gcal/period.

K1	is a coefficient that corrects for the increase of thermal energy requirements for DHW supply during the heating period (K1=1.25) and non-heating period (K1=1), calculated based on average temperature of cold water in the heating season (50C) and non-heating season (150C).

0,04	is a coefficient for convert cubic meters to Gcal.

mp	represents the number of working days in the period for which the baseline thermal energy consumption is calculated.

n	is the number of periods (usually – months, for new meter it is required – one week) over which the average consumption of thermal energy required for DHW supply has been calculated.

Gimet	denotes the consumption of water for DHW according to charges for period i, in m3/period.

miwp	is the number of working days during month i when DHW was supplied, excluding breaks such as school holidays.

The specific baseline consumption for DHW, in Gcal/working day, is also refined using the formula:

qDHW=1ni=1nGimetmiwp,  Gcal/working day

This formula is applied when there is a separate water meter installed specifically for DHW.

These refinements in the methodology ensure a more accurate and context-specific calculation of the baseline thermal energy consumption for DHW supply. By considering the presence or absence of a separate water meter and adjusting for seasonal variations in water temperature, the methodology becomes more adaptable to different operational conditions of the building.

#### Calculation of the baseline thermal energy consumption for heating

In situations where there is no separate metering unit for heating systems, and assuming that air-supply units are not operational, the monthly baseline thermal energy consumption required for heating systems is determined through a specific calculation process. This involves deducting the established baseline thermal energy consumption for DHW from the total thermal energy consumption as indicated in energy bills.

This calculation method considers several factors:

- Climate Conditions: The prevailing weather conditions during the observed periods are considered, as they significantly impact heating requirements.

- Heating Operation Days: The number of days the heating system was operational during the period under review.

- Normative Indoor Temperature: The standard or expected indoor temperature, which influences the energy demand for heating.

The objective is to ascertain the average monthly energy consumption of the building per Heating Degree Day (HDD). This approach closely aligns the thermal characteristics of the building with the specific climate conditions experienced during the observed periods.

To ensure accuracy and reliability of the data, any consumption figures that are either below 80% or exceed 200% of the average daily consumption are excluded from the analysis. Such deviations are often indicative of anomalies, such as system repairs or extraordinary circumstances, and their exclusion helps maintain the integrity of the calculation.

The following expressions are utilized to execute this refined calculation process:

QH=mp(tI-to,m)ni=1nQimet-QDHW,imiwp(tI-to,m,i),  Gcal/period

Where:

QH	is the baseline thermal energy consumption required for heating systems, Gcal/period.

mp	is the number of days during the і period, when heat supply required for heating systems has been in operation

tI	indicates the specified required indoor temperature

to,m,i	is the average registered (source: Serviciul Hidrometeorologic de Stat) ambient temperature over the period і

to,m	is the average ambient temperature over the month for which the baseline is calculated

miwp(tI-to,m,i)	is the number of degrees-days during the period і

miwp 	is the duration of the heating seasons [days]

n	indicates the number of periods

Qimet	is the total consumption of thermal energy by a building during the period і (only heating period months are included, October - April)

QDHW,i	is the baseline thermal consumption required for the DHW supply during the period і, calculated according to expressions in the previous chapter. If QDHW,i is based on separate heat meters for DHW QDHW,i=0

This methodology ensures a more precise and climate-sensitive assessment of the baseline thermal energy consumption for heating, providing a robust foundation for energy management and optimization strategies.

The specific baseline consumption for heating, in Gcal/degree day, is refined as follows:

qH=1nj=1nQimet-QHW,imiwp(ti-to,m,i),  Gcal/DD

#### Calculation of the baseline thermal energy consumption for ventilation

Typically, existing systems in these buildings are either non-operational or lack heat recovery capabilities. Therefore, to establish a realistic and effective baseline for thermal energy consumption for ventilation, the following considerations are made:

- Adjustment of energy needs for Ventilation: The baseline energy consumption is defined through standardized indoor conditions correlated to actual outside temperature which depending on building operation can lead to higher or lower energy consumption in comparison with the bills.

- Assessment of Current Systems: Understanding the limitations of existing ventilation systems, especially their lack of heat recovery functionality, is crucial in determining the baseline.

In order to calculate the BEC for ventilation two methods are available, depending on the availability of the measuring equipment at the facility:

- Method I – simplified, defining the Baseline thermal energy consumption for ventilation based on temperature.

- Method 2 – precise, defining the baseline thermal energy consumption for ventilation based on temperature and registered CO2 levels.

Note: In case of availability of CO2 sensors at the facility, than apply Method 2.

##### Method 1

The baseline thermal energy consumption for a period for ventilation is calculated using the following expression:

QVe,i=HVe∙nVe,i∙hVe∙tI-to,m,itI-to,Ve,i,  Gcal/period

Where:

Qv,e,i	is the baseline consumption for ventilation for the period i, in Gcal/period

HVe	is the heating capacity of the mechanical ventilation system, which incorporates the recuperation coefficient in case if exists, Gcal/hour

nVe,i	refers to the number of days the ventilation system is operational during the period i

hVe	is the average number of hours per day that the ventilation system operates

tI	is the specified required indoor temperature

to,m,i	indicates the average ambient temperature over the period і

to,Ve,i	refers to the outdoor design temperature for ventilation

The specific baseline thermal energy consumption for ventilation, in Gcal/degree hour, is refined as follows:

qVe,i=HVe∙1tI-to,Ve,i,  Gcal/degree hour

##### Method 2

When the measured CO2 levels exceed the standardized threshold (1000 ppm or more) during the operational period, it necessitates an adjustment in the calculation of energy consumption for ventilation. This adjustment accounts for the increased energy demand that arises from the need to maintain optimal air quality and temperature in environments with elevated CO2 levels.

The calculation for this additional heating consumption (in addition to the identified consumption for ventilation from the meter [Gcal/period]) is as follows:

QVe,i=0,0057∙mp∙ nVe,i∙hVe∙(tI-to,m,i)∙η∙Cco2-1000Cco2,  Gcal/period

Where:

QVe,i	represents the amount of additional heat energy per period for reducing the CO2 level in a building, measured in Gcal/period

0,0057	is coefficient that calculated as 0,33 kW/(K m3) x 20 m3/h / 1163 kWh/Gcal, there 0,33 (kW/(K m3)  - volume heat capacity of air, 20 (m3/h) amount of the fresh air for one person to guarantee that CO2 will be not more than 1000 pm, 1163 – coefficient to convert  from kWh to Gcal

mp	represents the average number of individuals present at the building during its operational hours

nVe,i	is the number of working days per verification period

hVe	indicates the average number of operating hours per day

tI	specifies the required indoor temperature for the building

to,m,i	is the average outdoor temperature over the period і

Cco2	represents the average measured CO2 level inside the building during the operational period, expressed in ppm

η	is the coefficient representing heat recovery, in case if none than η=1

This formula is designed to accurately quantify the amount of energy required for ventilation, directly attributable to the higher CO2 concentrations. This method ensures a more comprehensive and realistic assessment of the building's energy needs under varied environmental conditions.

### Calculation of the baseline electrical energy consumption

The baseline electrical energy consumption is determined as the average of the metered energy consumption over specified periods. This average is then used to calculate the daily electrical energy consumption for each month, serving as a foundational metric for subsequent calculations. These daily consumption figures are averaged to derive an average daily consumption rate for electricity, applicable for the entire month. However, any consumption figures that fall below 80% or exceed 200% of this average are excluded from the calculation to account for potential anomalies due to system repairs or extraordinary circumstances. The formula applied for this purpose is as follows:

eday,B,i=EEl,avg, met,ini, kWh/day

Where:

eday,B,i	represents the baseline specific electrical energy consumption per working day

EEl,avg, met,i	denotes the electrical energy consumption for a specific month (e.g., January), calculated over a three-year duration (e.g., three times the month of January)

ni	is the amount of all working days during a respective month (e.g., January, etc.) over a three-year period

This approach to calculating the baseline electrical energy consumption ensures a thorough and accurate assessment of energy usage patterns, laying the groundwork for effective energy management and optimization strategies.

## Verification

### Verification of thermal energy consumption (post Implementation)

The verification of thermal energy consumption is conducted by incorporating the following key elements:

- Climate Information - data pertaining to the climate for the specific verification period (month).

- Heating Usage - the number of days heating was operational during the verification period.

- DHW Usage - the number of days DHW was utilized in the verification period.

- Ventilation Usage - the number of days ventilation systems were in use during the verification period.

- Actual Consumption - the actual thermal energy consumption recorded in the verification period (month).

These first four inputs are essential to tailor the baseline thermal energy consumption to align with the climate conditions and usage data specific to the verification period. The baseline thermal energy for heating, DHW and ventilation is recalculated to reflect the climate conditions during the verification period, utilizing the formulas detailed in the preceding chapters.

The actual consumption data for the verification period is then compared with the recalculated baseline to determine the thermal energy savings achieved during this verification period. The following expression is employed to calculate these energy savings:

ESav,i=(QH,i,ad+QDHW,i,ad+QVe,i,ad)-QVer,i=QB,i,ad-QVer,i,  Gcal/period

Where:

ESav,i	represents the energy savings

QH,i,ad	is the baseline thermal energy consumption for heating, adapted for the climate conditions in the verification period

QDHW,i,ad	denotes the baseline thermal energy consumption for DHW, adapted for the conditions in the verification period

QVe,i,ad	is the baseline thermal energy consumption for ventilation, adapted for the conditions in the verification period

QVer,i	indicates the actual thermal energy consumption in the verification period

QB,i,ad	is the baseline thermal energy consumption, adapted for climate conditions in the verification period, which is equal to the sum of QH,i,ad+QDHW,i,ad+QVe,i,ad

This refined methodology ensures a comprehensive and accurate assessment of thermal energy savings, considering the specific conditions and actual usage during the verification period.

### Verification of electrical energy consumption

The verification of electrical energy consumption involves a comparison between the adapted baseline consumption (to the conditions of for the verification period and the actual electrical energy consumption recorded during that same period. The adaptation of the baseline consumption takes into account potential changes in the number of working days of the building, as well as variations in the number of operational hours per day.

The following formula is used for this adaptation:

EB,ad,i=eday,B,ihop,Verhop,Bni,Ver, kWh/period

Where:

eday,B,i	baseline specific electrical energy consumption for the verification month

EB,ad,i	is the baseline electrical energy consumption, adapted for conditions in the verification period

hop,Ver	represents the average of daily operation hours in the verification period

hop,B	are the average daily operation hours under baseline conditions

ni,Ver	denotes the number of days of operation in the verification period, (working days)

The electrical energy savings are then calculated by subtracting the actual electrical energy consumption during the verification period from the adapted baseline electrical energy consumption. The formula for this calculation is:

EEl, sav,i=EB,ad,i-EVer,i,  kWh/period

Where:

EEl, sav,i	indicates the achieved electrical energy savings

EB,ad,i	is the baseline electrical energy consumption, adapted for conditions in the verification period

EVer,i	is the actual electrical energy consumption during the verification period

This verification methodology provides a comprehensive and accurate assessment of electrical energy savings, taking into account the specific operational conditions of the building during the verification period.

### Verification of overall energy savings

In recognizing that heat and electricity are interchangeable in their use for heating and DHW systems, and with the ultimate goal of achieving cost savings in energy consumption, the overall savings are calculated in monetary terms using the following formula:

ETot,m,i=EEl, sav,i×Tel, i+ESav,i×Th,i,  MDL/period

Where:

ETot,m,i	total savings for the period i expressed in monetary units

EEl, sav,i	electricity savings for the period i, measures in kWh

ESav,i	heat (or fuel) savings for the period i, measured in Gcal

Tel, i	electricity tariff for the period i, in MDL per kWh

Th, i	heat tariff for the period i, in MDL per Gcal

This approach not only quantifies energy savings in financial terms but also incentivizes the Contractor to optimize the use of energy sources, aligning energy efficiency goals with cost-saving objectives.

## Methodology limitations and adjustment protocols

The methodology developed for energy consumption analysis has inherent limitations, particularly when significant alterations occur in the characteristics of the building under examination. These changes can substantially impact the accuracy and applicability of the model. The methodology requires adjustments in the scenarios described below.

### Criteria for recalculations

The baseline will be recalculated under the following conditions:

- A change in the building's heated area by more than 10%

- A change in the power of installed electrical equipment by more than 10%

- A change in the building's operating times by more than 20%

- A significant alteration in standard indoor comfort conditions (such as temperature, humidity, ventilation, and lighting)

- A notable change in the number of permanent and occasional occupants, particularly if this alters the number of occupants by more than 20% and is requested by the Contractor and agreed by the Employer

### Expansion or reduction of the building's heated area or occupancy

- For expansions post-renovation, it is advisable to install additional heat and electricity meters in the new sections of the building. The baseline will then be recalculated by combining the original heating energy consumption with the readings from these new meters.

- Alternatively, a new baseline can be established using the existing methodology. The new baseline includes the energy consumption after the implementation of the measures plus/minus the additional/reduced consumption as a result of the extension/reduction of the e.g. building’s heated area considering the Factors of Influence as described in the methodology.

### Complete repurposing of building usage

When a building undergoes a complete shift in its purpose, resulting in a different set of operating conditions, it becomes essential to make adjustments that accurately reflect the building's new function and usage patterns.

The original methodology may no longer provide accurate or relevant insights due to the altered energy dynamics of the building. Therefore, adapting the methodology to reflect these significant changes is crucial for maintaining its effectiveness and relevance in energy consumption analysis and verification.

In all cases, the energy monitoring system will be a crucial tool for recalculating and adjusting the baseline to align with the new conditions. This ensures that the methodology remains relevant and accurate, even in the face of significant changes to the building's structure, usage, or occupancy.