MeASUREMENT AND VERIFICATION PLAN
MESCO ToolBox

TABLE OF CONTENTS

1.	Introduction	3

2.	M&V Plan	3

2.1.	Scope, frequency, and forms for information transfer	3

2.1.1.	Information transfer from Employer to Contractor	3

2.1.2.	Outcomes of observation and data analysis	3

2.2.	Detailed procedures for data collection and analysis	4

2.2.1.	Heat consumption (Qah)	4

2.2.2.	Electricity consumption (Qael)	4

2.2.3.	Indoor temperature (tai)	4

2.2.4.	Outdoor temperature (tao)	4

2.2.5.	Carbon dioxide (CO2) levels at the Facility	5

2.3.	Calculation of Baseline Energy Consumption	5

2.3.1.	For each Verification month	5

2.3.2.	Adjustments for significant changes	6

2.4.	Calculation of actual energy savings level	6

2.4.1.	For each Verification month	6

2.4.2.	For the valid verification period	7

2.5.	Rules for Calculation in Case of Significant Changes	8

2.5.1.	Adjustments for Building Modifications	8

2.5.2.	Criteria for Recalculation	8

2.5.3.	Energy Audit Requirement	8

# Introduction

This M&V Plan outlines the methodology and procedures for the systematic observation, collection, processing, systematization, and analysis of information on the consumption of thermal and electrical energy, variables of Factors of Influence, calculation of Baseline Energy Consumption and actual Energy Savings Level at the Facility, Rules for calculation of Baseline Energy Consumption and actual Energy Savings Level at the Facility for the Verification Month and Valid Verification Period. The Plan includes:

- Guidelines on the scope, frequency, and forms for transferring verification-related information.

- Protocols for calculating Baseline Energy Consumption for each Verification Month.

- Methods for determining the actual Energy Savings Level at the Facility for each Verification Month.

- Comprehensive rules for calculating Baseline Energy Consumption and actual Energy Savings Level for the entire Valid Verification Period.

# M&V Plan

## Scope, frequency, and forms for information transfer

### Information transfer from Employer to Contractor

Within 5 (five) business days following each Verification Month, the Employer is required to provide the Contractor with:

- Actual outdoor temperature at the Facility

- Valid Verification Days for the Verification Month

- Total number of working days and operational hours on Valid Verification Days in the Verification Month

This information should be provided in accordance with FORM 1, which is included in the Appendix.

This section of the M&V Plan ensures that the Contractor receives timely and accurate operational data from the Employer, which is essential for effective measurement and verification of energy consumption and savings at the Facility.

### Outcomes of observation and data analysis

The Contractor is responsible for providing the Employer with information regarding the Baseline Energy Consumption and actual Energy Savings Level for the respective month, the list of Factors of Influence, their quantitative indicators, and readings of the metering units of heat and electricity installed at the Facility.

Within 6 (six) working days of receiving the relevant information from the Employer (as per FORM 1), the Contractor must submit detailed reports including:

- Baseline Energy Consumption and actual Energy Savings Level for the respective month,

- the list of Factors of Influence and their quantitative indicators, and

- the readings from the heat and electricity metering units installed at the Facility.

The information provided by the Contractor should adhere to the formats outlined in FORMS 2 and 3, which are attached in the Appendix.

## Detailed procedures for data collection and analysis

### Heat consumption (Qah)

The Contractor is tasked with the observation, collection, processing, systematization, and analysis of data related to the consumption of heat (Qah) at the Facility. This includes:

- Recording data from heat metering units installed at the facility for every day of the Verification Month, from 00:00 to 24:00.

- Ensuring the monitoring system is programmed to store these readings for at least 36 months, with remote access provided to the Employer.

### Electricity consumption (Qael)

The Contractor is tasked with the observation, collection, processing, systematization, and analysis of data related to the consumption of electricity (Qael) at the Facility. This includes:

- Recording data from electricity metering units installed at the facility for every day of the Verification Month, from 00:00 to 24:00.

- Ensuring the monitoring system is programmed to store these readings for at least 36 months, with remote access provided to the Employer.

### Indoor temperature (tai)

Indoor temperature (tai) at the Facility is determined as specific (average per hour) amount of all measured temperature values. The Contractor must:

- Measure and record indoor temperatures at least every 15 minutes each day of the Verification Month, ensuring an accuracy of up to 0.5°C. These measurements should be taken in 3 (three) specific premises agreed upon by both parties and 2 (two) or less determined by the Employer.

- Ensuring the device for information recording is programmed to store these records for at least 4 (four) months, with remote access provided to the Employer.

### Outdoor temperature (tao)

Outdoor temperature (tao) is determined as the mean outdoor temperature for Valid Verification Days in a respective Verification Month. The Contractor must:

- Determine the mean outdoor temperature for Valid Verification Days using data from the nearest meteorological post and temperature loggers.

### Carbon dioxide (CO2) levels at the Facility

The carbon dioxide levels at the Facility equipped with mechanical ventilation systems is determined as the mean per hour value of CO2 levels. The Contractor must monitor and record CO2 levels:

- CO2 measurements should be taken at least every 15 minutes each day, with an accuracy of up to 100 ppm. These readings are to be taken in up to three premises where a mechanical ventilation system shall be installed as determined by the Employer. Upon the Employer’s request the mentioned premises can be changed.

- The monitoring devices must be capable of storing these readings for at least 4 (four) months, with an electronic copy kept for at least 36 (thirty-six) months.

This section of the M&V Plan ensures comprehensive and accurate data collection, which is fundamental for the effective analysis of energy consumption and the calculation of energy savings at the Facility.

## Calculation of Baseline Energy Consumption

### For each Verification month

The Baseline Energy Consumption is calculated using a specific formula that considers various factors such as the heating characteristics of the Facility, specific energy consumption for ventilation, and standard indoor and outdoor temperatures. The formula is as follows:

Qbh=Qh×tsi-tao×nh+qv×nwd×hwh×tsi-taotsi-tso )-Qbhcor

Where:

Qbh	represents the Baseline Energy Consumption, in Gcal

Qh	is the Heating Characteristic of the Facility, in Gcal/HDD

qv	denotes specific energy consumption for ventilation, in Gcal/h

tsi	is the standard indoor temperature (average for all rooms), in °C

tao	is the average outdoor temperature, in °C

tso	is the standard outdoor temperature (for ventilation -100C), in °C

nh	is the number of Valid Verification Days, in days

nwd	is the number of working days, in days

hwh	is the average number of working hours per day, in hours

Qbhcor 	is the Ventilation Characteristic of the Facility, which shall be calculated according to the following formula:

Qbhcor = qv×nwd'×hwh'×tis-toatis-tos

Where:

nwd’	is the number of working days when CO2 levels were higher than the standard, in days

hwh’	is the average number of working hours per day when CO2 level was higher than the standard, in hours

qv	is the specific energy consumption for ventilation at a Facility, in Gcal/h

tao	is the average outdoor temperature during working days when CO2 level was higher than the standard, in °C

only for the Facility with a mechanical ventilation system and in case the CO2 level is more than the standard of 1,000 ppm during 3 (three) or more working hours per working day during a Verification Month. In other cases, value Qbhcor =0

### Adjustments for significant changes

In cases of significant changes during Energy Performance Contract implementation the Parties shall have the right to demand the recalculation of the amounts of the Factors of Influence (Heating Characteristics of a Facility (qh), specific energy consumption for ventilation (qv) and Electricity Characteristics of a Facility (qel(i))) and establish a new baseline. This includes expansions or reductions in the heated area, installation or reduction of equipment, and changes of the operational time or in building usage.

The recalculated baseline will account for the new conditions, either increasing or decreasing based on the specific changes made.

## Calculation of actual energy savings level

### For each Verification month

The actual Energy Savings Level at the Facility for a respective Verification Month is calculated as a percentage of the Baseline Energy Consumption, using the formula:

E%m=EQbhх100%

Where:

E%m	is the actual Energy Savings Level at the Facility for the respective Verification Month, in %

Qbh	is the Baseline Energy Consumption for a respective Verification Month, in Gcal

E	represents the total amount of saved/overconsumed energy at the Facility for a respective Verification Months, calculated as the sum of the savings/overconsumption for heat and electricity according to the formula below:

E=(Eh+Eel)

Where:

Eh	is the amount of saved/overconsumed heat for a respective Verification Month, in Gcal

Eel	is the amount of saved/overconsumed electricity for a respective Verification Month adjusted by the tariffs difference for heat and electricity, in Gcal

the amount of saved/overconsumed heat for a respective Verification Month:

Eh=Qbh-Qah

Where:

Qah 	is the actual amount of heat consumed for Valid Verification Days for a respective Verification Month, in Gcal

Qbh	represents the Baseline Energy Consumption for a respective Verification Month, in Gcal

and the amount of saved/overconsumed electricity for a respective Verification Month:

Eel=0, if (Qa el-QbelQb el×100 %<10%,

or

Eel=1163×Qbel-Qael×1163 ×TelTh,

if

(Qa el-QbelQb el×100 %≥10%

Where:

Tel	is the average, officially approved electricity tariff in a respective Verification Month, in MDL/kWh

Th	is the average, officially approved heat tariff in a respective Verification Month, in MDL/Gcal;

Qael	represents the actual amount of electricity consumed in a respective Verification Month (for verification days only), in kWh

Qbel	is the Baseline Electricity Consumption in a Verification Month, in kWh, which shall be calculated as the product of the Electricity Characteristics of a Facility (qel(i)) in kWh/working day) by the number of working days at the Verification Month (nwd):

Qbel= qel(i)×nwd

Where (i) stands for a particular month (January, February, March, April, October, November, or December).

### For the valid verification period

The actual Energy Savings Level at the Facility over the Valid Verification Period is calculated by aggregating the monthly savings and comparing them to the total Baseline Energy Consumption. The formula for this calculation is:

E%=j=1mEmjj=1mQbhj×100%

Where:

E%	the Actual Energy Saving Level at the Facility for the Valid Verification Period, in %

j	a Verification Month

m	the number of months during the Valid Verification Period

Qbhj	is the Baseline Energy Consumption at the Facility in jth Verification Month, in Gcal

Ejm	is the amount of saved/overconsumed energy at the Facility in jth Verification Month, in Gcal

## Rules for Calculation in Case of Significant Changes

### Adjustments for Building Modifications

In scenarios involving significant modifications to the building, such as an expansion or reduction of the heated area, or changes in the usage of electrical equipment, recalculations of the baseline and energy savings are necessary.

The recalculations will be based on the new operational conditions and characteristics of the Facility.

### Criteria for Recalculation

The recalculations should be considered if:

- A significant change in the building's heated area (more than 10%)

- A significant change in the power of installed electrical equipment (more than 10%)

- A significant change in the building's operating times (more than 20%)

- A significant change in the required standard internal comfort conditions (e.g., temperature, humidity, ventilation, lighting)

- A significant change in the number of occupants if this alters the number of occupants by more than 20%

These recalculations are initiated either by the Employer or the Contractor, with a relevant act drawn up to document the process.

### Energy Audit Requirement

If there is a growth or reduction in key aspects of the Facility's operation or structure by more than 15%, an additional energy audit is required. This audit will inform the recalculation of Factors of Influence, such as Heating Characteristics (qh), specific energy consumption for ventilation (qv), and Electricity Characteristics (qel(i)).

Appendixes:

FORM 1

FORM 2

FORM 3

FORM 4

FORM 5

Carbon dioxide (CO2) levels at the Facility (provided a mechanical ventilation system is installed at the premises)